## _2014_Municipal_Private_Sewage_
Propriétaire de l’installation | Adresse du site | Municipalité du site | Secteur | District | Contaminant | Type de dépassement | Date du début du dépassement | Date de la fin du dépassement | Limite du contaminant | Unité du contaminant | Fréquence de la limite | Nombre de dépassements | Minimum de la quantité | Maximum de la quantité | Mesure prise par l’installation | Mesure prise par le ministère
1319536 Ontario Ltd. - Royal Ontario Golf Course | 6378 Trafalgar Rd | Milton | Miscellaneous Communal | Halton-Peel | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 10 | mg/L | mon avg | 1 | 12 | 12 | Equipment Modified - Repaired - Replaced or Re-calibrated; New/Amended Approval; Operational Process Modification | Ticket Issued
1319536 Ontario Ltd. - Royal Ontario Golf Course | 6378 Trafalgar Rd | Milton | Miscellaneous Communal | Halton-Peel | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 460 | 460 | Equipment Modified - Repaired - Replaced or Re-calibrated; New/Amended Approval; Operational Process Modification | Ticket Issued
Burleigh Falls Inn & Suites Inc. -Burleigh Island Lodge | 4791 Hwy 28 Burleigh Falls | North Kawartha | Miscellaneous Communal | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-05-13 | 2014-05-13 | 2 | mg/L | /d | 1 | 2.6 | 2.6 | None Required; Other | Assessment Complete - No Action Required
Clublink Corporation - National Pines Golf Club | 8165 10th Sideroad | Innisfil | Miscellaneous Communal | Barrie | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 2.5 | mg/L | mon avg | 1 | 3.9 | 3.9 | New Equipment or Treatment Process Installed | Assessment Complete - No Action Required
ClubLink Corporation ULC - Emerald Hills Golf Club | 14001 Warden Ave Stouffville | Whitchurch-Stouffville | Miscellaneous Communal | York-Durham | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 296 | 296 | Action Plan Submitted - Implementing Improvements | Assessment Complete - Incident Resolved
Creg Quay Limited | Lot 21 Concession 1 Geographic township: Lancaster | South Glengarry | Miscellaneous Communal | Cornwall | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-11-14 | 2014-12-15 | 40 | mg/L | seasonal avg | 1 | 218 | 218 | Conducting Study | Assessment Underway
Crest Support Services (Meadowcrest) Inc. | 13570 Elginfield Rd | Lucan Biddulph | Miscellaneous Communal | London | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 1252 | 1252 | Additional Monitoring Underway | Assessment Complete - No Action Required
Detour Gold Corporation -Detour Lake Project - Construction Camp | Leased Mining Claim RW307, Unsurveyed Territory, District of Cochrane | Unsurveyed Territory (Timmins District Office) | Miscellaneous Communal | Timmins | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 0.5 | mg/L | mon avg | 1 | 0.611 | 0.611 | Conducting Study; Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Underway
Detour Gold Corporation -Detour Lake Project - Construction Camp | Leased Mining Claim RW307, Unsurveyed Territory, District of Cochrane | Unsurveyed Territory (Timmins District Office) | Miscellaneous Communal | Timmins | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 25 | mg/L | mon avg | 1 | 29.25 | 29.25 | Conducting Study; Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Underway
Envirosearch Operations Inc. - Mallorytown North ONroute Service Centre | Part Lots 15 16 & 17 Conc. 1 Geographic township: Yonge | Front of Yonge | Miscellaneous Communal | Kingston | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 0.3 | mg/L | mon avg | 1 | 0.315 | 0.315 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
Envirosearch Operations Inc. - Mallorytown North ONroute Service Centre | Part Lots 15 16 & 17 Conc. 1 Geographic township: Yonge | Front of Yonge | Miscellaneous Communal | Kingston | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 10 | mg/L | mon avg | 1 | 15.75 | 15.75 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
Envirosearch Operations Inc. - Mallorytown North ONroute Service Centre | Part Lots 15 16 & 17 Conc. 1 Geographic township: Yonge | Front of Yonge | Miscellaneous Communal | Kingston | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-12-01 | 2014-12-31 | 10 | mg/L | mon avg | 1 | 11 | 11 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
Grand River Conservation Authority - Guelph Lake Conservation Area | 7743 Conservation Dr RR #4 | Guelph/Eramosa | Miscellaneous Communal | Guelph | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-07-01 | 2014-08-31 | 10 | mg/L | mon avg | 2 | 13 | 26 | Ceased Operations; Conducting Study; Equipment Modified - Repaired - Replaced or Re-calibrated; New/Amended Approval; Operational Process Modification | Voluntary Abatement Program Underway
Grand River Conservation Authority - Guelph Lake Conservation Area | 7743 Conservation Dr RR #4 | Guelph/Eramosa | Miscellaneous Communal | Guelph | NITRATE (AS NITROGEN) | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 15 | mg/L | mon avg | 1 | 21.5 | 21.5 | Ceased Operations; Conducting Study; Equipment Modified - Repaired - Replaced or Re-calibrated; New/Amended Approval; Operational Process Modification | Voluntary Abatement Program Underway
Grand River Conservation Authority - Guelph Lake Conservation Area | 7743 Conservation Dr RR #4 | Guelph/Eramosa | Miscellaneous Communal | Guelph | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-06-01 | 2014-06-30 | 10 | mg/L | mon avg | 1 | 18.9 | 18.9 | Operational Process Modification | Assessment Complete - No Action Required
Grand River Conservation Authority - Guelph Lake Conservation Area | 7743 Conservation Dr RR #4 | Guelph/Eramosa | Miscellaneous Communal | Guelph | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-07-01 | 2014-08-31 | 10 | mg/L | mon avg | 2 | 32.5 | 59.4 | Ceased Operations; Conducting Study; Equipment Modified - Repaired - Replaced or Re-calibrated; New/Amended Approval; Operational Process Modification | Voluntary Abatement Program Underway
Hastings and Prince Edward District School Board -Bayside Secondary School | 1247 Old Highway 2 | Quinte West | Miscellaneous Communal | Peterborough | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-01-01 | 2014-01-31 | 1 | mg/L | mon avg | 1 | 2.24 | 2.24 | New/Amended Approval; New/Modified Sampling Program Underway | Other Abatement Action Taken
Hastings and Prince Edward District School Board -Bayside Secondary School | 1247 Old Highway 2 | Quinte West | Miscellaneous Communal | Peterborough | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-02-01 | 2014-02-28 | 1 | mg/L | mon avg | 1 | 1.53 | 1.53 | New Equipment or Treatment Process Installed; New/Amended Approval | Other Abatement Action Taken
Hastings and Prince Edward District School Board -Bayside Secondary School | 1247 Old Highway 2 | Quinte West | Miscellaneous Communal | Peterborough | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-02-01 | 2014-02-28 | 1 | mg/L | mon avg | 1 | 1.53 | 1.53 | New/Amended Approval | Other Abatement Action Taken
Hastings and Prince Edward District School Board -Bayside Secondary School | 1247 Old Highway 2 | Quinte West | Miscellaneous Communal | Peterborough | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-03-01 | 2014-03-31 | 1 | mg/L | mon avg | 1 | 1.78 | 1.78 | New/Amended Approval | Other Abatement Action Taken
Hastings and Prince Edward District School Board -Bayside Secondary School | 1247 Old Highway 2 | Quinte West | Miscellaneous Communal | Peterborough | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-04-01 | 2014-04-30 | 1 | mg/L | mon avg | 1 | 1.21 | 1.21 | New/Amended Approval | Other Abatement Action Taken
Hastings and Prince Edward District School Board -Bayside Secondary School | 1247 Old Highway 2 | Quinte West | Miscellaneous Communal | Peterborough | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-06-01 | 2014-06-30 | 1 | mg/L | mon avg | 1 | 3.71 | 3.71 | New/Amended Approval | Other Abatement Action Taken
Hastings and Prince Edward District School Board -Bayside Secondary School | 1247 Old Highway 2 | Quinte West | Miscellaneous Communal | Peterborough | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-08-01 | 2014-08-31 | 1 | mg/L | mon avg | 1 | 3 | 3 | New/Amended Approval | Other Abatement Action Taken
Hastings and Prince Edward District School Board -Bayside Secondary School | 1247 Old Highway 2 | Quinte West | Miscellaneous Communal | Peterborough | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-09-01 | 2014-09-30 | 1 | mg/L | mon avg | 1 | 3.29 | 3.29 | New/Amended Approval | Other Abatement Action Taken
Hastings and Prince Edward District School Board -Bayside Secondary School | 1247 Old Highway 2 | Quinte West | Miscellaneous Communal | Peterborough | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-10-01 | 2014-10-31 | 1 | mg/L | mon avg | 1 | 3.55 | 3.55 | New/Amended Approval | Other Abatement Action Taken
Hastings and Prince Edward District School Board -Bayside Secondary School | 1247 Old Highway 2 | Quinte West | Miscellaneous Communal | Peterborough | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-11-01 | 2014-11-30 | 1 | mg/L | mon avg | 1 | 3.89 | 3.89 | New/Amended Approval | Other Abatement Action Taken
Hastings and Prince Edward District School Board -Bayside Secondary School | 1247 Old Highway 2 | Quinte West | Miscellaneous Communal | Peterborough | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-12-01 | 2014-12-31 | 1 | mg/L | mon avg | 1 | 3.16 | 3.16 | New/Amended Approval | Other Abatement Action Taken
Her Majesty the Queen in Right of Ontario as Represented by the Minister of Infrastructure: Ontario Infrastructure and Lands Corporation - McFarlane Lake Wastewater Treatment Plant | 3737 Highway 69 S | Greater Sudbury | Miscellaneous Communal | Sudbury | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 15289 | 15289 | Additional Monitoring Underway; Operational Process Modification | Voluntary Abatement Program Underway
Her Majesty the Queen in Right of Ontario as Represented by the Minister of Infrastructure: Ontario Infrastructure and Lands Corporation - McFarlane Lake Wastewater Treatment Plant | 3737 Highway 69 S | Greater Sudbury | Miscellaneous Communal | Sudbury | FLOW | Approval/Permit Non-Compliance | 2014-04-15 | 2014-04-15 | 205 | m³ | /d | 1 | 633.7 | 633.7 | None Required | Assessment Complete - Incident Resolved; Assessment Complete - No Action Required
HK Travel Centres GP Inc. - Port Hope ONroute Service Station | Lot: 31 32, Concession: 2, Geographic Township: HOPE | Port Hope | Miscellaneous Communal | Peterborough | PH - LOW | Approval/Permit Non-Compliance | 2014-06-16 | 2014-06-16 | 6 | pH | any | 1 | 5.05 | 5.05 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
HK Travel Centres GP Inc. - Port Hope ONroute Service Station | Lot: 31 32, Concession: 2, Geographic Township: HOPE | Port Hope | Miscellaneous Communal | Peterborough | PH - LOW | Approval/Permit Non-Compliance | 2014-08-11 | 2014-08-11 | 6 | pH | any | 1 | 5.59 | 5.59 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - No Action Required
HK Travel Centres GP Inc. - Port Hope ONroute Service Station | Lot: 31 32, Concession: 2, Geographic Township: HOPE | Port Hope | Miscellaneous Communal | Peterborough | PH - LOW | Approval/Permit Non-Compliance | 2014-08-26 | 2014-08-26 | 6 | pH | any | 1 | 4.95 | 4.95 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
HK Travel Centres GP Inc. - Port Hope ONroute Service Station | Lot: 31 32, Concession: 2, Geographic Township: HOPE | Port Hope | Miscellaneous Communal | Peterborough | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 0.3 | mg/L | mon avg | 1 | 0.684 | 0.684 | Training/Procedure Change | Assessment Underway
HK Travel Centres GP Inc. - Port Hope ONroute Service Station | Lot: 31 32, Concession: 2, Geographic Township: HOPE | Port Hope | Miscellaneous Communal | Peterborough | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-31 | 10 | mg/L | mon avg | 1 | 17 | 17 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Underway
HK Travel Centres GP Inc. operating as HK Travel Centres L.P. - Mallorytown North ONroute Service Centre | Part Lots 15 16 & 17 Conc. 1 Geographic township: Yonge | Front of Yonge | Miscellaneous Communal | Kingston | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 10 | mg/L | mon avg | 1 | 10.75 | 10.75 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
HK Travel Centres GP Inc. operating as HK Travel Centres L.P. - Mallorytown North ONroute Service Centre | Part Lots 15 16 & 17 Conc. 1 Geographic township: Yonge | Front of Yonge | Miscellaneous Communal | Kingston | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 10 | mg/L | mon avg | 1 | 13 | 13 | Operational Process Modification | Assessment Complete - Incident Resolved; Assessment Complete - No Action Required; Voluntary Abatement Program Underway
HMS Host -Ingersoll Travel Plaza | 401 West Bound | South-West Oxford | Miscellaneous Communal | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 5 | mg/L | mon avg | 1 | 18.6 | 18.6 | None Required | Assessment Complete - No Action Required
HMS Host -Ingersoll Travel Plaza | 401 West Bound | South-West Oxford | Miscellaneous Communal | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 5 | mg/L | mon avg | 1 | 34.2 | 34.2 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - No Action Required
HMS Host -Ingersoll Travel Plaza | 401 West Bound | South-West Oxford | Miscellaneous Communal | London | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 10 | mg/L | mon avg | 1 | 14.5 | 14.5 | None Required | Assessment Complete - No Action Required
Lake Avenue Resort Park Inc. | 37-38 Lake Avenue Lane | Prince Edward | Miscellaneous Communal | Belleville | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-05-30 | 2014-05-30 | 3 | mg/L | any | 1 | 5 | 5 | Action Plan Submitted - Implementing Improvements | Assessment Underway
Lake Avenue Resort Park Inc. | 37-38 Lake Avenue Lane | Prince Edward | Miscellaneous Communal | Belleville | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-08-29 | 2014-08-29 | 3 | mg/L | any | 1 | 10 | 10 | Action Plan Submitted - Implementing Improvements | Assessment Underway
Lake Avenue Resort Park Inc. | 37-38 Lake Avenue Lane | Prince Edward | Miscellaneous Communal | Belleville | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-09-16 | 2014-09-16 | 3 | mg/L | any | 1 | 9.65 | 9.65 | Action Plan Submitted - Implementing Improvements | Assessment Underway
Lake Avenue Resort Park Inc. | 37-38 Lake Avenue Lane | Prince Edward | Miscellaneous Communal | Belleville | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-05-30 | 2014-05-30 | 10 | mg/L | any | 1 | 11 | 11 | Action Plan Submitted - Implementing Improvements | Assessment Underway
Mini Lakes Residents Association | 34 - 7541 Wellington County Rd | Puslinch | Miscellaneous Communal | Guelph | NITRATE (AS NITROGEN) | Approval/Permit Non-Compliance | 2013-03-01 | 2014-02-28 | 5 | mg/L | rolling annual avg | 1 | 5.04 | 5.04 | Additional Monitoring Underway | Assessment Complete - No Action Required
Niagara Peninsula Conservation Authority - Ball's Falls Visitor Centre | 3172 Sixth Ave Jordan | Lincoln | Miscellaneous Communal | Niagara | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 10 | mg/L | mon avg | 1 | 11 | 11 | None Required | Other Abatement Action Taken
Niagara Peninsula Conservation Authority - Ball's Falls Visitor Centre | 3172 Sixth Ave Jordan | Lincoln | Miscellaneous Communal | Niagara | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 10 | mg/L | mon avg | 1 | 122 | 122 | Operational Process Modification | Assessment Underway
Niagara Peninsula Conservation Authority - Ball's Falls Visitor Centre | 3172 Sixth Ave Jordan | Lincoln | Miscellaneous Communal | Niagara | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 10 | mg/L | mon avg | 1 | 70 | 70 | Operational Process Modification | Assessment Underway
Niagara Peninsula Conservation Authority - Ball's Falls Visitor Centre | 3172 Sixth Ave Jordan | Lincoln | Miscellaneous Communal | Niagara | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-31 | 10 | mg/L | mon avg | 1 | 23 | 23 | Operational Process Modification | Assessment Underway
Niagara Peninsula Conservation Authority - Ball's Falls Visitor Centre | 3172 Sixth Ave Jordan | Lincoln | Miscellaneous Communal | Niagara | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 10 | mg/L | mon avg | 1 | 11 | 11 | Operational Process Modification | Assessment Underway
Niagara Peninsula Conservation Authority - Ball's Falls Visitor Centre | 3172 Sixth Ave Jordan | Lincoln | Miscellaneous Communal | Niagara | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 10 | mg/L | mon avg | 1 | 12 | 12 | None Required | Other Abatement Action Taken
Niagara Peninsula Conservation Authority - Ball's Falls Visitor Centre | 3172 Sixth Ave Jordan | Lincoln | Miscellaneous Communal | Niagara | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 10 | mg/L | mon avg | 1 | 18 | 18 | Operational Process Modification | Assessment Underway
Niagara Peninsula Conservation Authority - Ball's Falls Visitor Centre | 3172 Sixth Ave Jordan | Lincoln | Miscellaneous Communal | Niagara | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 10 | mg/L | mon avg | 1 | 21 | 21 | Operational Process Modification | Assessment Underway
Niagara Peninsula Conservation Authority - Ball's Falls Visitor Centre | 3172 Sixth Ave Jordan | Lincoln | Miscellaneous Communal | Niagara | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-06-01 | 2014-06-30 | 10 | mg/L | mon avg | 1 | 11 | 11 | Operational Process Modification | Assessment Underway
Niagara Peninsula Conservation Authority - Ball's Falls Visitor Centre | 3172 Sixth Ave Jordan | Lincoln | Miscellaneous Communal | Niagara | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 10 | mg/L | mon avg | 1 | 13 | 13 | Operational Process Modification | Assessment Underway
Rio Can Property Services - Orillia Square Mall | 1029 Brodie Dr | Orillia | Miscellaneous Communal | Barrie | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 0.3 | mg/L | mon avg | 1 | 0.97 | 0.97 | Equipment Modified - Repaired - Replaced or Re-calibrated | Voluntary Abatement Program Underway
Sudbury Condominium Corporation #5 - Willisville Sewage Treatment Plant | Part of 13, Concession: 2, Geographic Township: Curtin | Curtin | Miscellaneous Communal | Sudbury | BIOCHEMICAL OXYGEN DEMAND | Policy/Guideline Non-Conformance | 2014-01-01 | 2014-12-31 | 25 | mg/L | annual avg | 1 | 57.3 | 57.3 | Additional Monitoring Underway; Conducting Study; Operational Process Modification | Assessment Underway; Voluntary Abatement Program Underway
Sudbury Condominium Corporation #5 - Willisville Sewage Treatment Plant | Part of 13, Concession: 2, Geographic Township: Curtin | Curtin | Miscellaneous Communal | Sudbury | TOTAL SUSPENDED SOLIDS | Policy/Guideline Non-Conformance | 2014-01-01 | 2014-12-31 | 25 | mg/L | annual avg | 1 | 26.8 | 26.8 | Additional Monitoring Underway; Conducting Study; Operational Process Modification | Assessment Underway; Voluntary Abatement Program Underway
The Brockville Society of the Standard Church of America/Weslayan Church of Canada | 3545 County Road No. 27 | Elizabethtown-Kitley | Miscellaneous Communal | Kingston | NITRATE (AS NITROGEN) | Approval/Permit Non-Compliance | 2014-06-17 | 2014-06-17 | 2.5 | mg/L | /quart | 1 | 7.65 | 7.65 | Conducting Study | Voluntary Abatement Program Underway
The Corporation of the City of Greater Sudbury - Azilda Wastewater Treatment Plant | 564 St. Agnes St Azilda | Greater Sudbury | Municipal Sewage | Sudbury | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 468 | 468 | Additional Monitoring Underway; Operational Process Modification | Assessment Complete - Incident Resolved
The Corporation of the City of Greater Sudbury - Azilda Wastewater Treatment Plant | 564 St. Agnes St Azilda | Greater Sudbury | Municipal Sewage | Sudbury | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 5 | mg/L | mon avg | 1 | 9.36 | 9.36 | Additional Monitoring Underway | Assessment Complete - No Action Required
The Corporation of the City of Greater Sudbury - Azilda Wastewater Treatment Plant | 564 St. Agnes St Azilda | Greater Sudbury | Municipal Sewage | Sudbury | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 5 | mg/L | mon avg | 1 | 26.56 | 26.56 | Operational Process Modification | Assessment Underway
The Corporation of the City of Greater Sudbury - Azilda Wastewater Treatment Plant | 564 St. Agnes St Azilda | Greater Sudbury | Municipal Sewage | Sudbury | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 10 | mg/L | mon avg | 1 | 18.8 | 18.8 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the City of Greater Sudbury - Azilda Wastewater Treatment Plant | 564 St. Agnes St Azilda | Greater Sudbury | Municipal Sewage | Sudbury | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 10 | mg/L | mon avg | 1 | 13.1 | 13.1 | Operational Process Modification; Other | Assessment Complete - Incident Resolved
The Corporation of the City of Greater Sudbury - Capreol Lagoon | Lot 11 Concession 6, Geographic Township: CAPREOL | Greater Sudbury | Municipal Sewage | Sudbury | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-01-01 | 2014-12-31 | 1.38 | mg/L | annual avg | 1 | 1.59 | 1.59 | Equipment Modified - Repaired - Replaced or Re-calibrated | Other Abatement Action Taken
The Corporation of the City of Greater Sudbury - Chelmsford Sewage Treatment Plant | 300 Laurette St | Greater Sudbury | Municipal Sewage | Sudbury | FLOW | Approval/Permit Non-Compliance | 2014-10-15 | 2014-10-15 | 18200 | m³ | /d | 1 | 26420 | 26420 | None Required | Assessment Complete - No Action Required
The Corporation of the City of Greater Sudbury - Chelmsford Sewage Treatment Plant | 300 Laurette St | Greater Sudbury | Municipal Sewage | Sudbury | FLOW | Approval/Permit Non-Compliance | 2014-10-16 | 2014-10-16 | 18200 | m³ | /d | 1 | 30500 | 30500 | None Required | Assessment Complete - No Action Required
The Corporation of the City of Greater Sudbury - Chelmsford Sewage Treatment Plant | 300 Laurette St | Greater Sudbury | Municipal Sewage | Sudbury | FLOW | Approval/Permit Non-Compliance | 2014-10-17 | 2014-10-17 | 18200 | m³ | /d | 1 | 31390 | 31390 | None Required | Assessment Complete - No Action Required
The Corporation of the City of Greater Sudbury - Chelmsford Sewage Treatment Plant | 300 Laurette St | Greater Sudbury | Municipal Sewage | Sudbury | FLOW | Approval/Permit Non-Compliance | 2014-10-18 | 2014-10-18 | 18200 | m³ | /d | 1 | 18320 | 18320 | None Required | Assessment Complete - No Action Required
The Corporation of the City of Greater Sudbury - Walden Sewage Treatment Plant | Lot 10 Conc. 3 Geographic Township: Waters | Greater Sudbury | Municipal Sewage | Sudbury | PH - LOW | Approval/Permit Non-Compliance | 2014-03-11 | 2014-03-11 | 6 | pH | any | 1 | 5.9 | 5.9 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - No Action Required
The Corporation of the City of Greater Sudbury - Walden Sewage Treatment Plant | Lot 10 Conc. 3 Geographic Township: Waters | Greater Sudbury | Municipal Sewage | Sudbury | PH - LOW | Approval/Permit Non-Compliance | 2014-03-11 | 2014-03-11 | 6 | pH | /wk | 1 | 5.9 | 5.9 | Operational Process Modification | Other Abatement Action Taken
The Corporation of the City of Greater Sudbury - Walden Sewage Treatment Plant | Lot 10 Conc. 3 Geographic Township: Waters | Greater Sudbury | Municipal Sewage | Sudbury | PH - LOW | Approval/Permit Non-Compliance | 2014-07-05 | 2014-07-05 | 6 | pH | /wk | 1 | 5.7 | 5.7 | Operational Process Modification | Other Abatement Action Taken
The Corporation of the City of Hamilton - Dundas Wastewater Treatment Plant | 135 King St W Dundas | Hamilton | Municipal Sewage | Hamilton | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-02-06 | 2014-02-06 | 9.1 | kg/d | 24hr | 1 | 9.2 | 9.2 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the City of Kawartha Lakes -Lindsay Water Pollution Control Plant | 48 Lagoon St Lindsay | Kawartha Lakes | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 3 | mg/L | mon avg | 1 | 3.4 | 3.4 | Operational Process Modification | Assessment Complete - Incident Resolved
The Corporation of the City of Kawartha Lakes -Lindsay Water Pollution Control Plant | 48 Lagoon St Lindsay | Kawartha Lakes | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 64.5 | kg/d | mon avg | 1 | 83.94 | 83.94 | Equipment Modified - Repaired - Replaced or Re-calibrated | Other Abatement Action Taken
The Corporation of the City of Kawartha Lakes -Lindsay Water Pollution Control Plant | 48 Lagoon St Lindsay | Kawartha Lakes | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 3 | mg/L | mon avg | 1 | 6 | 6 | Equipment Modified - Repaired - Replaced or Re-calibrated | Other Abatement Action Taken
The Corporation of the City of Kingston - Cana Wastewater Treatment Plant | 1756 Cana Blvd | Kingston | Municipal Sewage | Kingston | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-02-01 | 2014-02-28 | 1 | mg/L | mon avg | 1 | 1.03 | 1.03 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the City of Kingston - Cana Wastewater Treatment Plant | 1756 Cana Blvd | Kingston | Municipal Sewage | Kingston | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-06-01 | 2014-06-30 | 1 | mg/L | mon avg | 1 | 1.01 | 1.01 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the City of Kingston - Cana Wastewater Treatment Plant | 1756 Cana Blvd | Kingston | Municipal Sewage | Kingston | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-09-01 | 2014-09-30 | 1 | mg/L | mon avg | 1 | 1.04 | 1.04 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the City of London - Greenway WPCP | 109 Greenside Ave | London | Municipal Sewage | London | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-09-01 | 2014-09-30 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 209 | 209 | New Equipment or Treatment Process Installed | Assessment Complete - Incident Resolved
The Corporation of the City of London -Pottersburg WWTP | 1141 Hamilton Rd | London | Municipal Sewage | London | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-08-01 | 2014-08-31 | 0.75 | mg/L | mon avg | 1 | 0.86 | 0.86 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the City of Quinte West - Frankford Water Pollution Control Plant | 174 Trent St N Frankford | Quinte West | Municipal Sewage | Peterborough | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 0.7 | kg/d | mon avg | 1 | 0.83 | 0.83 | Other | Other Abatement Action Taken; Voluntary Abatement Program Underway
The Corporation of the City of Quinte West - Frankford Water Pollution Control Plant | 174 Trent St N Frankford | Quinte West | Municipal Sewage | Peterborough | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 70 | kg/d | mon avg | 1 | 106.1 | 106.1 | Other | Other Abatement Action Taken; Voluntary Abatement Program Underway
The Corporation of the City of Quinte West - Trenton Water Pollution Control Plant | 25 Couch Cres Trenton | Quinte West | Municipal Sewage | Peterborough | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-09-01 | 2014-09-30 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 340 | 340 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - No Action Required
The Corporation of the City of Quinte West - Trenton Water Pollution Control Plant | 25 Couch Cres Trenton | Quinte West | Municipal Sewage | Peterborough | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 397.5 | kg/d | mon avg | 1 | 482.4 | 482.4 | Other | Other Abatement Action Taken; Voluntary Abatement Program Underway
The Corporation of the City of Sarnia - Sarnia Water Pollution Control Centre | 333 St. Andrews St | Sarnia | Municipal Sewage | Sarnia | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 227.64 | 227.64 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the City of Sarnia - Sarnia Water Pollution Control Centre | 333 St. Andrews St | Sarnia | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 309 | kg/d | mon avg | 1 | 401 | 401 | None Required | Assessment Complete - Incident Resolved
The Corporation of the City of Sarnia - Sarnia Water Pollution Control Centre | 333 St. Andrews St | Sarnia | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 8 | mg/L | mon avg | 1 | 13.48 | 13.48 | None Required | Assessment Complete - Incident Resolved
The Corporation of the City of Sarnia - Sarnia Water Pollution Control Centre | 333 St. Andrews St | Sarnia | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 8 | mg/L | mon avg | 1 | 12.62 | 12.62 | Operational Process Modification | Assessment Complete - Incident Resolved
The Corporation of the City of Sarnia - Sarnia Water Pollution Control Centre | 333 St. Andrews St | Sarnia | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 309 | kg/d | mon avg | 1 | 366 | 366 | Operational Process Modification | Assessment Complete - Incident Resolved
The Corporation of the City of Sarnia -Brights Grove Lagoons | Lot: 3-5, Concession: 9, Geographic Township: SARNIA, Sarnia, City, County of Lambton | Sarnia | Municipal Sewage | Sarnia | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-08-01 | 2014-08-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 232 | 232 | Conducting Study | Assessment Underway; Other Abatement Action Taken
The Corporation of the City of Sarnia -Brights Grove Lagoons | Lot: 3-5, Concession: 9, Geographic Township: SARNIA, Sarnia, City, County of Lambton | Sarnia | Municipal Sewage | Sarnia | PH - LOW | Approval/Permit Non-Compliance | 2014-07-17 | 2014-11-17 | 7 | pH | any | 5 | 6.4 | 6.93 | Conducting Study | Assessment Underway; Other Abatement Action Taken
The Corporation of the City of Sarnia -Brights Grove Lagoons | Lot: 3-5, Concession: 9, Geographic Township: SARNIA, Sarnia, City, County of Lambton | Sarnia | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-16 | 2014-05-28 | 3 | mg/L | /d | 7 | 4.51 | 19.5 | Conducting Study; New/Modified Sampling Program Underway | Assessment Underway; Other Abatement Action Taken
The Corporation of the City of Sarnia -Brights Grove Lagoons | Lot: 3-5, Concession: 9, Geographic Township: SARNIA, Sarnia, City, County of Lambton | Sarnia | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-16 | 2014-05-28 | 6.1 | kg/d | /d | 7 | 8.21 | 35.51 | Conducting Study; New/Modified Sampling Program Underway | Assessment Underway; Other Abatement Action Taken
The Corporation of the City of Sarnia -Brights Grove Lagoons | Lot: 3-5, Concession: 9, Geographic Township: SARNIA, Sarnia, City, County of Lambton | Sarnia | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-10-22 | 2014-10-29 | 6.1 | kg | /d | 2 | 6.4 | 8.9 | Conducting Study; New/Modified Sampling Program Underway | Assessment Underway; Other Abatement Action Taken
The Corporation of the City of Sarnia -Brights Grove Lagoons | Lot: 3-5, Concession: 9, Geographic Township: SARNIA, Sarnia, City, County of Lambton | Sarnia | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-10-22 | 2014-10-29 | 3 | mg/L | /d | 2 | 3.52 | 4.86 | Conducting Study; New/Modified Sampling Program Underway | Assessment Underway; Other Abatement Action Taken
The Corporation of the City of Sarnia -Brights Grove Lagoons | Lot: 3-5, Concession: 9, Geographic Township: SARNIA, Sarnia, City, County of Lambton | Sarnia | Municipal Sewage | Sarnia | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-10-01 | 2014-11-17 | 10 | mg/L | mon avg | 2 | 10.5 | 13.5 | Conducting Study; New/Modified Sampling Program Underway | Assessment Underway; Other Abatement Action Taken
The Corporation of the City of Temiskaming Shores - Haileybury Wastewater Treatment Plant | 100 View St | Haileybury | Municipal Sewage | North Bay | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 827 | 827 | Operational Process Modification | Other Abatement Action Taken
The Corporation of the City of Temiskaming Shores - Haileybury Wastewater Treatment Plant | 100 View St | Haileybury | Municipal Sewage | North Bay | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-08-01 | 2014-08-30 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 5628.5 | 5628.5 | Operational Process Modification | Other Abatement Action Taken
The Corporation of the City of Temiskaming Shores - Haileybury Wastewater Treatment Plant | 100 View St | Haileybury | Municipal Sewage | North Bay | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-09-01 | 2014-09-30 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 8819 | 8819 | Operational Process Modification | Other Abatement Action Taken
The Corporation of the City of Temiskaming Shores - Haileybury Wastewater Treatment Plant | 100 View St | Haileybury | Municipal Sewage | North Bay | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 1668 | 1668 | Operational Process Modification | Other Abatement Action Taken
The Corporation of the City of Toronto - Highland Creek WWTP | 51 Beechgrove Dr | Toronto | Municipal Sewage | Toronto | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 1 | mg/L | mon avg | 1 | 1.1 | 1.1 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the County of Brant - Cainsville Lagoons | 30 Shaver St | Brant | Municipal Sewage | Guelph | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-04-17 | 2014-04-17 | 30 | mg/L | any | 1 | 35 | 35 | None Required | Assessment Complete - No Action Required
The Corporation of the County of Brant - Cainsville Lagoons | 30 Shaver St | Brant | Municipal Sewage | Guelph | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-11-10 | 2014-11-10 | 30 | mg/L | any | 1 | 41 | 41 | None Required | Assessment Complete - No Action Required
The Corporation of the County of Brant - Cainsville Lagoons | 30 Shaver St | Brant | Municipal Sewage | Guelph | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-12-15 | 2014-12-15 | 30 | mg/L | any | 1 | 37 | 37 | None Required | Assessment Complete - No Action Required
The Corporation of the County of Oxford - Drumbo WPCP | 93 Peterson St | Blandford-Blenheim | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 3 | mg/L | mon avg | 1 | 4.25 | 4.25 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the County of Oxford - Drumbo WPCP | 93 Peterson St | Blandford-Blenheim | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 0.8 | mg/L | mon avg | 1 | 1.686 | 1.686 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the County of Oxford - Norwich STP | Stover St S | Norwich | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-15 | 2014-04-15 | 5 | mg/L | /d | 1 | 6.3 | 6.3 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the County of Oxford - Norwich STP | Stover St S | Norwich | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-16 | 2014-04-16 | 5 | mg/L | /d | 1 | 6.1 | 6.1 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the County of Oxford - Norwich STP | Stover St S | Norwich | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-23 | 2014-04-23 | 5 | mg/L | /d | 1 | 6.6 | 6.6 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the County of Oxford - Norwich STP | Stover St S | Norwich | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-25 | 2014-04-25 | 5 | mg/L | /d | 1 | 5.3 | 5.3 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the County of Oxford - Norwich STP | Stover St S | Norwich | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 3 | mg/L | mon avg | 1 | 4.1 | 4.1 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the County of Oxford - Norwich STP | Stover St S | Norwich | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-05-07 | 2014-05-07 | 5 | mg/L | /d | 1 | 6.3 | 6.3 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the County of Prince Edward - Picton Wastewater Treatment Plant | 60 Church St Picton | Prince Edward | Municipal Sewage | Belleville | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 0.8 | mg/L | mon avg | 1 | 0.93 | 0.93 | Training/Procedure Change | Assessment Underway
The Corporation of the County of Prince Edward - Wellington Water Pollution Control Plant | 460 Wellington Main St | Prince Edward | Municipal Sewage | Belleville | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 25 | mg/L | mon avg | 1 | 33.6 | 33.6 | None Required | Assessment Complete - No Action Required
The Corporation of the County of Prince Edward - Wellington Water Pollution Control Plant | 460 Wellington Main St | Prince Edward | Municipal Sewage | Belleville | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 37.5 | kg/d | mon avg | 1 | 43.46 | 43.46 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Arran-Elderslie - Chesley Sewage Works | Lot: 27 & 28, Concession: 2, Geographic Township: ELDERSLIE, Arran-Elderslie, Municipality, County of Bruce | Arran-Elderslie | Municipal Sewage | Owen Sound | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 11 | kg/d | mon avg | 30 | 19.6 | 19.6 | None Required | Voluntary Abatement Program Underway
The Corporation of the Municipality of Bluewater -Bayfield Sewage Works | Jowett Lane Long Hill Rd | Bluewater | Municipal Sewage | Owen Sound | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 812 | 812 | Training/Procedure Change | Assessment Complete - Incident Resolved
The Corporation of the Municipality of Bluewater -Bayfield Sewage Works | Jowett Lane Long Hill Rd | Bluewater | Municipal Sewage | Owen Sound | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 362 | 362 | Training/Procedure Change | Assessment Complete - Incident Resolved
The Corporation of the Municipality of Bluewater -Zurich Sewage Lagoons | Main Street (CR84) | Bluewater | Municipal Sewage | Owen Sound | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 15 | mg/L | mon avg | 1 | 20 | 20 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Brighton -Brighton Lagoon | 100 County Road 64 | Brighton | Municipal Sewage | Peterborough | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 1 | mg/L | mon avg | 1 | 1.39 | 1.39 | Action Plan Submitted - Implementing Improvements; Conducting Study; Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of Brighton -Brighton Lagoon | 100 County Road 64 | Brighton | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 17 | mg/L | mon avg | 1 | 20.7 | 20.7 | Action Plan Submitted - Implementing Improvements; Conducting Study; Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of Brighton -Brighton Lagoon | 100 County Road 64 | Brighton | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 17 | mg/L | mon avg | 1 | 20 | 20 | Conducting Study; New/Modified Sampling Program Underway; Operational Process Modification | Assessment Underway; Voluntary Abatement Program Underway
The Corporation of the Municipality of Brighton -Brighton Lagoon | 100 County Road 64 | Brighton | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-06-01 | 2014-06-30 | 14 | mg/L | mon avg | 1 | 14.2 | 14.2 | Action Plan Submitted - Implementing Improvements; Conducting Study | Assessment Underway; Other Abatement Action Taken
The Corporation of the Municipality of Brighton -Brighton Lagoon | 100 County Road 64 | Brighton | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 14 | mg/L | mon avg | 1 | 21.8 | 21.8 | Conducting Study | Assessment Underway; Provincial Officer's Order Issued
The Corporation of the Municipality of Brighton -Brighton Lagoon | 100 County Road 64 | Brighton | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-08-01 | 2014-08-31 | 14 | mg/L | mon avg | 1 | 20.9 | 20.9 | Conducting Study | Assessment Underway; Provincial Officer's Order Issued
The Corporation of the Municipality of Brighton -Brighton Lagoon | 100 County Road 64 | Brighton | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-09-01 | 2014-09-30 | 14 | mg/L | mon avg | 1 | 18.1 | 18.1 | Conducting Study | Assessment Underway
The Corporation of the Municipality of Brighton -Brighton Lagoon | 100 County Road 64 | Brighton | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 64 | kg/d | mon avg | 1 | 71.2 | 71.2 | Conducting Study; New/Amended Approval | Assessment Underway; Other Abatement Action Taken; Provincial Officer's Order Issued
The Corporation of the Municipality of Brighton -Brighton Lagoon | 100 County Road 64 | Brighton | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-08-01 | 2014-08-31 | 64 | kg/d | mon avg | 1 | 69.3 | 69.3 | Conducting Study; New/Amended Approval | Assessment Underway; Provincial Officer's Order Issued
The Corporation of the Municipality of Brighton -Brighton Lagoon | 100 County Road 64 | Brighton | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 14 | mg/L | mon avg | 1 | 20.3 | 20.3 | Additional Monitoring Underway; Conducting Study | Assessment Underway
The Corporation of the Municipality of Brighton -Brighton Lagoon | 100 County Road 64 | Brighton | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 64 | kg/d | mon avg | 1 | 85.5 | 85.5 | Conducting Study; New/Amended Approval | Provincial Officer's Order Issued
The Corporation of the Municipality of Brighton -Brighton Lagoon | 100 County Road 64 | Brighton | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 17 | mg/L | mon avg | 1 | 21.93 | 21.93 | Action Plan Submitted - Implementing Improvements; Conducting Study | Assessment Underway; Provincial Officer's Order Issued
The Corporation of the Municipality of Brighton -Brighton Lagoon | 100 County Road 64 | Brighton | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-12-01 | 2014-12-31 | 17 | mg/L | mon avg | 1 | 20.3 | 20.3 | Action Plan Submitted - Implementing Improvements; Conducting Study | Assessment Underway; Voluntary Abatement Program Underway
The Corporation of the Municipality of Brooke-Alvinston - Alvinston Sewage Treatment Plant | 3084 River St | Brooke-Alvinston | Municipal Sewage | Sarnia | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 215 | 215 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - No Action Required
The Corporation of the Municipality of Central Elgin -Port Stanley Sewage Treatment Plant | 37575 Scotch Line | Central Elgin | Municipal Sewage | London | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-08-01 | 2014-08-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 565 | 565 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Central Elgin -Port Stanley Sewage Treatment Plant | 37575 Scotch Line | Central Elgin | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-31 | 3 | mg/L | mon avg | 1 | 4.05 | 4.05 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Municipality of Central Huron - Clinton Sewage Teatment Plant | 32 Walker St | Central Huron | Municipal Sewage | Owen Sound | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 31 | kg/d | mon avg | 1 | 53.3 | 53.3 | Equipment Modified - Repaired - Replaced or Re-calibrated; New Equipment or Treatment Process Installed; New/Amended Approval | Voluntary Abatement Program Underway
The Corporation of the Municipality of Central Manitoulin - Mindemoya Water Pollution Control Plant | Lot: 22, Concession: 6, Geographic Township: CARNARVON, Central Manitoulin | Central Manitoulin | Municipal Sewage | Sudbury | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 5 | mg/L | mon avg | 1 | 10.35 | 10.35 | Operational Process Modification | Assessment Complete - No Action Required; Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 328 | 328 | Action Plan Submitted - Implementing Improvements | Assessment Complete - Incident Resolved
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-18 | 2014-03-31 | 5 | mg/L | mon avg | 1 | 12.1 | 12.1 | Training/Procedure Change | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-19 | 2014-03-19 | 8 | mg/L | any | 1 | 19 | 19 | Training/Procedure Change | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-21 | 2014-03-21 | 8 | mg/L | any | 1 | 11 | 11 | Training/Procedure Change | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-22 | 2014-03-22 | 8 | mg/L | any | 1 | 15 | 15 | Training/Procedure Change | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-23 | 2014-03-23 | 8 | mg/L | any | 1 | 13 | 13 | Training/Procedure Change | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-24 | 2014-03-24 | 8 | mg/L | any | 1 | 14 | 14 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-25 | 2014-03-25 | 8 | mg/L | any | 1 | 12 | 12 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-26 | 2014-03-26 | 8 | mg/L | any | 1 | 14 | 14 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-27 | 2014-03-27 | 8 | mg/L | any | 1 | 11 | 11 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-28 | 2014-03-28 | 8 | mg/L | any | 1 | 12 | 12 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-29 | 2014-03-29 | 8 | mg/L | any | 1 | 8.4 | 8.4 | Ceased Operations | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-14 | 2014-04-28 | 5 | mg/L | any | 3 | 14 | 15 | None Required | Assessment Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-05-28 | 2014-05-28 | 5 | mg/L | any | 1 | 5.4 | 5.4 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 3 | mg/L | mon avg | 1 | 11.56 | 11.56 | None Required | Assessment Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-07 | 2014-04-07 | 8 | mg/L | any | 1 | 8.7 | 8.7 | None Required | Assessment Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-06-01 | 2014-06-30 | 3 | mg/L | mon avg | 1 | 4.25 | 4.25 | None Required | Assessment Underway
The Corporation of the Municipality of Chatham-Kent - Blenheim Lagoon | 19818 Lagoon Rd | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-06-02 | 2014-06-23 | 5 | mg/L | any | 4 | 5.3 | 7.7 | None Required | Assessment Underway
The Corporation of the Municipality of Chatham-Kent - Tilbury Sewage Treatment Plant | 20925 Clouthier St | Chatham-Kent | Municipal Sewage | Windsor | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 0.5 | mg/L | mon avg | 1 | 0.56 | 0.56 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Chatham-Kent - Tilbury Sewage Treatment Plant | 20925 Clouthier St | Chatham-Kent | Municipal Sewage | Windsor | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 0.5 | mg/L | mon avg | 1 | 0.56 | 0.56 | Additional Monitoring Underway; Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Tilbury Sewage Treatment Plant | 20925 Clouthier St | Chatham-Kent | Municipal Sewage | Windsor | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 0.5 | mg/L | mon avg | 1 | 0.67 | 0.67 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Chatham-Kent - Tilbury Sewage Treatment Plant | 20925 Clouthier St | Chatham-Kent | Municipal Sewage | Windsor | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 0.5 | mg/L | mon avg | 1 | 0.67 | 0.67 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent - Tilbury Sewage Treatment Plant | 20925 Clouthier St | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-12-01 | 2014-12-31 | 4 | mg/L | mon avg | 1 | 5.64 | 5.64 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Chatham-Kent - Tilbury Sewage Treatment Plant | 20925 Clouthier St | Chatham-Kent | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-12-01 | 2014-12-31 | 4 | mg/L | mon avg | 1 | 5.64 | 5.64 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Chatham-Kent -Chatham Water Pollution Control Plant | 100 Irwin St | Chatham-Kent | Municipal Sewage | Windsor | TOTAL RESIDUAL CHLORINE | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 0.01 | mg/L | mon avg | 1 | 0.02 | 0.02 | None Required | Voluntary Abatement Program Underway
The Corporation of the Municipality of Chatham-Kent -Chatham Water Pollution Control Plant | 100 Irwin St | Chatham-Kent | Municipal Sewage | Windsor | TOTAL RESIDUAL CHLORINE | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 0.01 | mg/L | mon avg | 1 | 0.02 | 0.02 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Dutton/Dunwich - Dutton Wastewater Treatment Plant | Concession A, Lot 10 | Dutton/Dunwich | Municipal Sewage | London | PH - LOW | Approval/Permit Non-Compliance | 2014-01-07 | 2014-01-07 | 6 | pH | any | 1 | 5.57 | 5.57 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Dutton/Dunwich - Dutton Wastewater Treatment Plant | Concession A, Lot 10 | Dutton/Dunwich | Municipal Sewage | London | PH - LOW | Approval/Permit Non-Compliance | 2014-04-29 | 2014-04-29 | 6 | pH | any | 1 | 5.17 | 5.17 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Dutton/Dunwich - Dutton Wastewater Treatment Plant | Concession A, Lot 10 | Dutton/Dunwich | Municipal Sewage | London | PH - LOW | Approval/Permit Non-Compliance | 2014-06-17 | 2014-06-17 | 6 | pH | any | 1 | 5.3 | 5.3 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Dutton/Dunwich - Dutton Wastewater Treatment Plant | Concession A, Lot 10 | Dutton/Dunwich | Municipal Sewage | London | PH - LOW | Approval/Permit Non-Compliance | 2014-07-22 | 2014-07-22 | 6 | pH | any | 1 | 5.93 | 5.93 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Dutton/Dunwich - Dutton Wastewater Treatment Plant | Concession A, Lot 10 | Dutton/Dunwich | Municipal Sewage | London | PH - LOW | Approval/Permit Non-Compliance | 2014-08-05 | 2014-08-05 | 6 | pH | any | 1 | 4.9 | 4.9 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Dutton/Dunwich - Dutton Wastewater Treatment Plant | Concession A, Lot 10 | Dutton/Dunwich | Municipal Sewage | London | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-08-01 | 2014-08-31 | 0.5 | mg/L | mon avg | 1 | 0.88 | 0.88 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Municipality of Dutton/Dunwich - Dutton Wastewater Treatment Plant | Concession A, Lot 10 | Dutton/Dunwich | Municipal Sewage | London | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-08-01 | 2014-08-31 | 0.5 | mg/L | mon avg | 1 | 0.88 | 0.88 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Dutton/Dunwich - Dutton Wastewater Treatment Plant | Concession A, Lot 10 | Dutton/Dunwich | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 5 | mg/L | mon avg | 1 | 9.3 | 9.3 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Municipality of Dutton/Dunwich - Dutton Wastewater Treatment Plant | Concession A, Lot 10 | Dutton/Dunwich | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 5 | mg/L | mon avg | 1 | 9.3 | 9.3 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Municipality of Dutton/Dunwich - Dutton Wastewater Treatment Plant | Concession A, Lot 10 | Dutton/Dunwich | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 5 | mg/L | mon avg | 1 | 10.2 | 10.2 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Municipality of Grey Highlands -Flesherton Sewage Treatment Plant | Lot: Part Lots 145 & 146, Concession: 1 WTSR, Geographic Township: ARTEMESIA | Grey Highlands | Municipal Sewage | Owen Sound | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-01-16 | 2014-01-31 | 4 | mg/L | mon avg | 2 | 9.55 | 15.1 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Municipality of Highlands East -Cardiff Sewage Works | Geographic Twp. of Bicroft | Highlands East | Municipal Sewage | Peterborough | HYDROGEN SULFIDE | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 0.1 | mg/L | mon avg | 1 | 0.78 | 0.78 | Other | Assessment Underway
The Corporation of the Municipality of Huron East - Seaforth Sewage Treatment Plant | 79468 Hannah Line | Huron East | Municipal Sewage | Owen Sound | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 28.5 | kg/d | mon avg | 1 | 39 | 39 | Ceased Operations | Assessment Complete - No Action Required
The Corporation of the Municipality of Huron East - Seaforth Sewage Treatment Plant | 79468 Hannah Line | Huron East | Municipal Sewage | Owen Sound | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 15 | mg/L | mon avg | 1 | 16.6 | 16.6 | Ceased Operations | Assessment Complete - No Action Required
The Corporation of the Municipality of Huron East -Brussels Wastewater Treatment Plant | Lot: 7, Concession: 5 Morris, Geographic Township: GREY | Huron East | Municipal Sewage | Owen Sound | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-04-01 | 2014-12-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 4 | 249 | 1493 | Equipment Modified - Repaired - Replaced or Re-calibrated; None Required | Assessment Complete - Incident Resolved
The Corporation of the Municipality of Huron East -Brussels Wastewater Treatment Plant | Lot: 7, Concession: 5 Morris, Geographic Township: GREY | Huron East | Municipal Sewage | Owen Sound | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 15 | kg/d | mon avg | 1 | 17.6 | 17.6 | Equipment Modified - Repaired - Replaced or Re-calibrated; None Required | Assessment Complete - Incident Resolved
The Corporation of the Municipality of Kincardine -Bruce Energy Centre Sewage Treatment Plant | Part 5 Plan 3R-7015 | Kincardine | Municipal Sewage | Owen Sound | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-09-10 | 2014-09-10 | 1.5 | mg/L | /d | 1 | 1.51 | 1.51 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of Lambton Shores - Forest Sewage Treatment Plant | 7550 Brush Rd | Lambton Shores | Municipal Sewage | Sarnia | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 536 | 536 | None Required | Voluntary Abatement Program Underway
The Corporation of the Municipality of Lambton Shores - Forest Sewage Treatment Plant | 7550 Brush Rd | Lambton Shores | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 5 | mg/L | mon avg | 1 | 23.02 | 23.02 | None Required | Voluntary Abatement Program Underway
The Corporation of the Municipality of Lambton Shores - Forest Sewage Treatment Plant | 7550 Brush Rd | Lambton Shores | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 9 | kg/d | mon avg | 1 | 26.1 | 26.1 | None Required | Voluntary Abatement Program Underway
The Corporation of the Municipality of Lambton Shores - Forest Sewage Treatment Plant | 7550 Brush Rd | Lambton Shores | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 5 | mg/L | mon avg | 1 | 28.68 | 28.68 | None Required | Voluntary Abatement Program Underway
The Corporation of the Municipality of Lambton Shores - Forest Sewage Treatment Plant | 7550 Brush Rd | Lambton Shores | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 9 | kg/d | mon avg | 1 | 30 | 30 | None Required | Voluntary Abatement Program Underway
The Corporation of the Municipality of Lambton Shores - Forest Sewage Treatment Plant | 7550 Brush Rd | Lambton Shores | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 5 | mg/L | mon avg | 1 | 19.13 | 19.13 | None Required | Voluntary Abatement Program Underway
The Corporation of the Municipality of Lambton Shores - Forest Sewage Treatment Plant | 7550 Brush Rd | Lambton Shores | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 9 | kg/d | mon avg | 1 | 22.3 | 22.3 | None Required | Voluntary Abatement Program Underway
The Corporation of the Municipality of Lambton Shores - Forest Sewage Treatment Plant | 7550 Brush Rd | Lambton Shores | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 5 | mg/L | mon avg | 1 | 16.6 | 16.6 | None Required | Voluntary Abatement Program Underway
The Corporation of the Municipality of Lambton Shores - Forest Sewage Treatment Plant | 7550 Brush Rd | Lambton Shores | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 9 | kg/d | mon avg | 1 | 21.1 | 21.1 | None Required | Voluntary Abatement Program Underway
The Corporation of the Municipality of Lambton Shores - Forest Sewage Treatment Plant | 7550 Brush Rd | Lambton Shores | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-31 | 3 | mg/L | mon avg | 1 | 3.61 | 3.61 | None Required | Voluntary Abatement Program Underway
The Corporation of the Municipality of Lambton Shores - Forest Sewage Treatment Plant | 7550 Brush Rd | Lambton Shores | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-09-01 | 2014-09-30 | 3 | mg/L | mon avg | 1 | 16.07 | 16.07 | Additional Monitoring Underway; New/Modified Sampling Program Underway | Assessment Underway
The Corporation of the Municipality of Lambton Shores - Forest Sewage Treatment Plant | 7550 Brush Rd | Lambton Shores | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 3 | mg/L | mon avg | 1 | 11.44 | 11.44 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of Leamington - Leamington Pollution Control Centre | 435 Seacliff Dr E | Leamington | Municipal Sewage | Windsor | BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 15 | mg/L | mon avg | 1 | 18.9 | 18.9 | Additional Monitoring Underway | Assessment Underway
The Corporation of the Municipality of Leamington - Leamington Pollution Control Centre | 435 Seacliff Dr E | Leamington | Municipal Sewage | Windsor | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 15 | mg/L | mon avg | 1 | 24.6 | 24.6 | Additional Monitoring Underway | Assessment Underway
The Corporation of the Municipality of Leamington - Leamington Pollution Control Centre | 435 Seacliff Dr E | Leamington | Municipal Sewage | Windsor | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 525 | kg/d | mon avg | 1 | 597 | 597 | Additional Monitoring Underway | Assessment Underway
The Corporation of the Municipality of Leamington - Leamington Pollution Control Centre | 435 Seacliff Dr E | Leamington | Municipal Sewage | Windsor | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 15 | mg/L | mon avg | 1 | 26 | 26 | Additional Monitoring Underway | Assessment Underway
The Corporation of the Municipality of Leamington - Leamington Pollution Control Centre | 435 Seacliff Dr E | Leamington | Municipal Sewage | Windsor | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 525 | kg/d | mon avg | 1 | 535 | 535 | Additional Monitoring Underway | Assessment Complete - Incident Resolved
The Corporation of the Municipality of Leamington - Leamington Pollution Control Centre | 435 Seacliff Dr E | Leamington | Municipal Sewage | Windsor | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 15 | mg/L | mon avg | 1 | 25 | 25 | Additional Monitoring Underway | Assessment Underway
The Corporation of the Municipality of Marmora and Lake - Deloro Sewage Treatment Facility | Village of Deloro | Marmora and Lake | Municipal Sewage | Belleville | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-01-01 | 2014-01-31 | 1 | mg/L | mon avg | 1 | 2.35 | 2.35 | New Equipment or Treatment Process Installed; New/Amended Approval | Additional Requirements Added in Approval/Permit
The Corporation of the Municipality of Marmora and Lake - Deloro Sewage Treatment Facility | Village of Deloro | Marmora and Lake | Municipal Sewage | Belleville | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-02-01 | 2014-02-28 | 1 | mg/L | mon avg | 1 | 2.32 | 2.32 | New Equipment or Treatment Process Installed; New/Amended Approval | Additional Requirements Added in Approval/Permit
The Corporation of the Municipality of Marmora and Lake - Deloro Sewage Treatment Facility | Village of Deloro | Marmora and Lake | Municipal Sewage | Belleville | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-03-01 | 2014-03-31 | 1 | mg/L | mon avg | 1 | 2.61 | 2.61 | New Equipment or Treatment Process Installed; New/Amended Approval | Additional Requirements Added in Approval/Permit
The Corporation of the Municipality of Marmora and Lake - Deloro Sewage Treatment Facility | Village of Deloro | Marmora and Lake | Municipal Sewage | Belleville | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-04-01 | 2014-04-30 | 1 | mg/L | mon avg | 1 | 1.57 | 1.57 | New/Amended Approval; New/Modified Sampling Program Underway | Additional Requirements Added in Approval/Permit
The Corporation of the Municipality of Marmora and Lake - Deloro Sewage Treatment Facility | Village of Deloro | Marmora and Lake | Municipal Sewage | Belleville | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-05-01 | 2014-05-31 | 1 | mg/L | mon avg | 1 | 1.97 | 1.97 | New/Amended Approval; New/Modified Sampling Program Underway | Additional Requirements Added in Approval/Permit
The Corporation of the Municipality of Marmora and Lake - Deloro Sewage Treatment Facility | Village of Deloro | Marmora and Lake | Municipal Sewage | Belleville | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-06-01 | 2014-06-30 | 1 | mg/L | mon avg | 1 | 2.22 | 2.22 | New/Amended Approval; New/Modified Sampling Program Underway | Additional Requirements Added in Approval/Permit
The Corporation of the Municipality of Marmora and Lake - Deloro Sewage Treatment Facility | Village of Deloro | Marmora and Lake | Municipal Sewage | Belleville | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-07-01 | 2014-07-31 | 1 | mg/L | mon avg | 1 | 2.17 | 2.17 | New/Amended Approval; New/Modified Sampling Program Underway | Additional Requirements Added in Approval/Permit
The Corporation of the Municipality of Marmora and Lake - Deloro Sewage Treatment Facility | Village of Deloro | Marmora and Lake | Municipal Sewage | Belleville | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-08-01 | 2014-08-31 | 1 | mg/L | mon avg | 1 | 2.29 | 2.29 | New Equipment or Treatment Process Installed; New/Amended Approval | Additional Requirements Added in Approval/Permit
The Corporation of the Municipality of Marmora and Lake - Deloro Sewage Treatment Facility | Village of Deloro | Marmora and Lake | Municipal Sewage | Belleville | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-09-01 | 2014-09-30 | 1 | mg/L | mon avg | 1 | 1.96 | 1.96 | New/Amended Approval | Additional Requirements Added in Approval/Permit
The Corporation of the Municipality of Marmora and Lake - Deloro Sewage Treatment Facility | Village of Deloro | Marmora and Lake | Municipal Sewage | Belleville | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-11-01 | 2014-11-30 | 1 | mg/L | mon avg | 1 | 2.46 | 2.46 | New Equipment or Treatment Process Installed; New/Amended Approval | Additional Requirements Added in Approval/Permit
The Corporation of the Municipality of Marmora and Lake - Deloro Sewage Treatment Facility | Village of Deloro | Marmora and Lake | Municipal Sewage | Belleville | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-10-01 | 2014-10-31 | 1 | mg/L | mon avg | 1 | 2.32 | 2.32 | New Equipment or Treatment Process Installed; New/Amended Approval | Additional Requirements Added in Approval/Permit
The Corporation of the Municipality of Marmora and Lake - Deloro Sewage Treatment Facility | Village of Deloro | Marmora and Lake | Municipal Sewage | Belleville | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-12-01 | 2014-12-31 | 1 | mg/L | mon avg | 1 | 2.03 | 2.03 | Equipment Modified - Repaired - Replaced or Re-calibrated; New/Amended Approval | Additional Requirements Added in Approval/Permit
The Corporation of the Municipality of North Grenville - Kemptville Water Pollution Control Plant | 2899 County Road 43 | North Grenville | Municipal Sewage | Kingston | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-06-01 | 2014-06-30 | 15 | mg/L | mon avg | 1 | 19.5 | 19.5 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the Municipality of North Grenville - Kemptville Water Pollution Control Plant | 2899 County Road 43 | North Grenville | Municipal Sewage | Kingston | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 15 | mg/L | mon avg | 1 | 19.3 | 19.3 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the Municipality of North Middlesex - Ailsa Craig WPCP | 4381 Elginfield Rd | North Middlesex | Municipal Sewage | London | PH - LOW | Approval/Permit Non-Compliance | 2014-08-22 | 2014-08-26 | 6.5 | pH | any | 5 | 6.25 | 6.25 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Municipality of North Middlesex - Ailsa Craig WPCP | 4381 Elginfield Rd | North Middlesex | Municipal Sewage | London | PH - LOW | Approval/Permit Non-Compliance | 2014-09-02 | 2014-09-06 | 6.5 | pH | any | 4 | 6.06 | 6.06 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Municipality of North Middlesex - Ailsa Craig WPCP | 4381 Elginfield Rd | North Middlesex | Municipal Sewage | London | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 10 | mg/L | mon avg | 1 | 10.8 | 10.8 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Municipality of North Perth -Listowel Waste Water Treatment Plant | 6115 Elma Line 84 | North Perth | Municipal Sewage | London | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 279 | 279 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the Municipality of North Perth -Listowel Waste Water Treatment Plant | 6115 Elma Line 84 | North Perth | Municipal Sewage | London | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 10 | mg/L | mon avg | 1 | 13.5 | 13.5 | Equipment Modified - Repaired - Replaced or Re-calibrated; Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Municipality of Powassan - Powassan WPCP | Lot: 17 & 18, Concession: 13, Geographic Township: Powassan | Powassan | Municipal Sewage | North Bay | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-06-16 | 2014-07-02 | 62.5 | kg/d | seasonal avg | 1 | 72.7 | 72.7 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the Municipality of Powassan - Powassan WPCP | Lot: 17 & 18, Concession: 13, Geographic Township: Powassan | Powassan | Municipal Sewage | North Bay | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-06-16 | 2014-07-02 | 25 | mg/L | seasonal avg | 1 | 29.4 | 29.4 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the Municipality of Sioux Lookout - Sioux Lookout Pollution Control Plant | 159 King St W | Sioux Lookout | Municipal Sewage | Kenora | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 807 | 807 | New/Modified Sampling Program Underway | Voluntary Abatement Program Underway
The Corporation of the Municipality of South Bruce - Teeswater Wastewater Treatment Plant | 245 Sideroad 10 A Teeswater & Formosa | South Bruce | Municipal Sewage | Owen Sound | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 0.15 | mg/L | mon avg | 1 | 0.159 | 0.159 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of South Bruce - Teeswater Wastewater Treatment Plant | 245 Sideroad 10 A Teeswater & Formosa | South Bruce | Municipal Sewage | Owen Sound | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 0.15 | mg/L | mon avg | 1 | 0.158 | 0.158 | None Required | Assessment Complete - No Action Required
The Corporation of the Municipality of South Bruce - Teeswater Wastewater Treatment Plant | 245 Sideroad 10 A Teeswater & Formosa | South Bruce | Municipal Sewage | Owen Sound | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 0.15 | mg/L | mon avg | 1 | 0.22 | 0.22 | Additional Monitoring Underway | Assessment Complete - Incident Resolved
The Corporation of the Municipality of South Bruce - Teeswater Wastewater Treatment Plant | 245 Sideroad 10 A Teeswater & Formosa | South Bruce | Municipal Sewage | Owen Sound | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-12-01 | 2014-12-31 | 0.15 | mg/L | mon avg | 1 | 0.175 | 0.175 | Equipment Modified - Repaired - Replaced or Re-calibrated; Operational Process Modification | Assessment Complete - Incident Resolved
The Corporation of the Municipality of South Huron - Exeter Sewage Treatment Facility | Lot: Part Lot 24 Lot 25, Concession: II, South Huron, Municipality, County of Huron | South Huron | Municipal Sewage | Owen Sound | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 239 | 239 | Additional Monitoring Underway | Assessment Complete - No Action Required
The Corporation of the Municipality of Strathroy-Caradoc - Mount Brydges Sewage Treatment Plant | 22416 Mill Rd Lot 20 Conc. 1 Ref. Plan 33R-12975 | Strathroy-Caradoc | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 3 | mg/L | mon avg | 1 | 10.18 | 10.18 | Equipment Modified - Repaired - Replaced or Re-calibrated | Voluntary Abatement Program Underway
The Corporation of the Municipality of Strathroy-Caradoc - Strathroy Sewage Treatment Plant | 27886 & 27888 Pike Road | Adelaide Metcalfe | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-06-01 | 2014-06-30 | 2 | mg/L | mon avg | 1 | 2.08 | 2.08 | Additional Monitoring Underway | Assessment Complete - Incident Resolved
The Corporation of the Municipality of Temagami - Temagami North Lagoon | 37 Cedar Ave | Temagami | Municipal Sewage | North Bay | PH - HIGH | Approval/Permit Non-Compliance | 2014-05-14 | 2014-05-14 | 9.5 | pH | any | 1 | 9.66 | 9.66 | Additional Monitoring Underway; New/Amended Approval; Operational Process Modification | Assessment Underway
The Corporation of the Municipality of Temagami - Temagami North Lagoon | 37 Cedar Ave | Temagami | Municipal Sewage | North Bay | PH - HIGH | Approval/Permit Non-Compliance | 2014-07-14 | 2014-07-24 | 9.5 | pH | any | 5 | 9.69 | 10.01 | Additional Monitoring Underway; New/Amended Approval; Operational Process Modification | Assessment Underway; Voluntary Abatement Program Underway
The Corporation of the Municipality of Thames Centre -Dorchester WPCP | 4835 Hamilton Rd | Thames Centre | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 4 | mg/L | mon avg | 1 | 4.35 | 4.35 | Equipment Modified - Repaired - Replaced or Re-calibrated; Other | Assessment Complete - No Action Required
The Corporation of the Municipality of Trent Hills -Campbellford Wastewater Treatment Plant | 22 Trent Dr Campbellford | Trent Hills | Municipal Sewage | Peterborough | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-06-01 | 2014-10-15 | 5 | mg/L | seasonal avg | 1 | 6.25 | 6.25 | Operational Process Modification | Assessment Underway
The Corporation of the Municipality of West Elgin - Rodney WPCP | 22590 Pioneer Line | West Elgin | Municipal Sewage | London | AMMONIA, UNIONIZED | Approval/Permit Non-Compliance | 2014-02-20 | 2014-02-20 | 0.1 | mg/L | any | 1 | 0.4 | 0.4 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the Municipality of West Elgin - Rodney WPCP | 22590 Pioneer Line | West Elgin | Municipal Sewage | London | AMMONIA, UNIONIZED | Approval/Permit Non-Compliance | 2014-03-04 | 2014-03-04 | 0.1 | mg/L | any | 1 | 0.58 | 0.58 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of West Elgin - Rodney WPCP | 22590 Pioneer Line | West Elgin | Municipal Sewage | London | AMMONIA, UNIONIZED | Approval/Permit Non-Compliance | 2014-03-19 | 2014-03-19 | 0.1 | mg/L | any | 1 | 0.23 | 0.23 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of West Elgin - Rodney WPCP | 22590 Pioneer Line | West Elgin | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 5 | mg/L | mon avg | 1 | 9 | 9 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the Municipality of West Elgin - Rodney WPCP | 22590 Pioneer Line | West Elgin | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 2.2 | kg/d | mon avg | 1 | 3.4 | 3.4 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the Municipality of West Elgin - Rodney WPCP | 22590 Pioneer Line | West Elgin | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 2.2 | kg/d | mon avg | 1 | 6.4 | 6.4 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of West Elgin - Rodney WPCP | 22590 Pioneer Line | West Elgin | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 5 | mg/L | mon avg | 1 | 14.4 | 14.4 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Municipality of West Nipissing - Field Sewage Treatment Plant | Lot: 14, Concession: 5 Geographic Township: Field | West Nipissing | Municipal Sewage | North Bay | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 25 | mg/L | mon avg | 1 | 28.8 | 28.8 | New/Amended Approval | Assessment Complete - Incident Resolved
The Corporation of the Municipality of West Nipissing - Field Sewage Treatment Plant | Lot: 14, Concession: 5 Geographic Township: Field | West Nipissing | Municipal Sewage | North Bay | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 0.66 | kg | /d | 1 | 1.4 | 1.4 | New/Amended Approval | Assessment Complete - Incident Resolved
The Corporation of the Municipality of West Nipissing - Field Sewage Treatment Plant | Lot: 14, Concession: 5 Geographic Township: Field | West Nipissing | Municipal Sewage | North Bay | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 0.03 | kg | /d | 1 | 0.05 | 0.05 | New/Amended Approval | Assessment Complete - Incident Resolved
The Corporation of the Municipality of West Nipissing - Field Sewage Treatment Plant | Lot: 14, Concession: 5 Geographic Township: Field | West Nipissing | Municipal Sewage | North Bay | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 25 | mg/L | mon avg | 1 | 35 | 35 | New/Amended Approval | Assessment Complete - Incident Resolved
The Corporation of the Municipality of West Nipissing - Field Sewage Treatment Plant | Lot: 14, Concession: 5 Geographic Township: Field | West Nipissing | Municipal Sewage | North Bay | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 0.66 | kg | /d | 1 | 1.7 | 1.7 | New/Amended Approval | Assessment Complete - Incident Resolved
The Corporation of the Separated Town of Smiths Falls - Smiths Falls Water Pollution Control Plant | 180 Queen St South of Highway 43 at Hershey Drive | Smiths Falls | Municipal Sewage | Ottawa | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 0.3 | mg/L | mon avg | 1 | 0.31 | 0.31 | Other | Assessment Complete - No Action Required
The Corporation of the Separated Town of Smiths Falls - Smiths Falls Water Pollution Control Plant | 180 Queen St South of Highway 43 at Hershey Drive | Smiths Falls | Municipal Sewage | Ottawa | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 15 | mg/L | mon avg | 1 | 15.73 | 15.73 | Other | Assessment Complete - No Action Required
The Corporation of the Town of Amherstburg - Edgewater Beach Lagoon | 1063 Front St N Lot 21 Concession 1 | Amherstburg | Municipal Sewage | Windsor | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 30 | mg/L | mon avg | 1 | 46 | 46 | Action Plan Submitted - Implementing Improvements; Other | Provincial Officer's Order Issued
The Corporation of the Town of Amherstburg - Edgewater Beach Lagoon | 1063 Front St N Lot 21 Concession 1 | Amherstburg | Municipal Sewage | Windsor | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 30 | mg/L | mon avg | 1 | 53.556 | 53.556 | Action Plan Submitted - Implementing Improvements; Other | Provincial Officer's Order Issued
The Corporation of the Town of Amherstburg - Edgewater Beach Lagoon | 1063 Front St N Lot 21 Concession 1 | Amherstburg | Municipal Sewage | Windsor | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-06-01 | 2014-06-30 | 30 | mg/L | mon avg | 1 | 33.625 | 33.625 | Action Plan Submitted - Implementing Improvements; Other | Provincial Officer's Order Issued
The Corporation of the Town of Amherstburg - Edgewater Beach Lagoon | 1063 Front St N Lot 21 Concession 1 | Amherstburg | Municipal Sewage | Windsor | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 8652 | 8652 | Action Plan Submitted - Implementing Improvements | Provincial Officer's Order Issued
The Corporation of the Town of Amherstburg - Edgewater Beach Lagoon | 1063 Front St N Lot 21 Concession 1 | Amherstburg | Municipal Sewage | Windsor | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 24429 | 24429 | Action Plan Submitted - Implementing Improvements | Provincial Officer's Order Issued
The Corporation of the Town of Amherstburg - Edgewater Beach Lagoon | 1063 Front St N Lot 21 Concession 1 | Amherstburg | Municipal Sewage | Windsor | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 1 | mg/L | mon avg | 1 | 2.165 | 2.165 | Action Plan Submitted - Implementing Improvements; Other | Provincial Officer's Order Issued
The Corporation of the Town of Amherstburg - Edgewater Beach Lagoon | 1063 Front St N Lot 21 Concession 1 | Amherstburg | Municipal Sewage | Windsor | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 1 | mg/L | mon avg | 1 | 2.019 | 2.019 | Action Plan Submitted - Implementing Improvements | Provincial Officer's Order Issued
The Corporation of the Town of Amherstburg - Edgewater Beach Lagoon | 1063 Front St N Lot 21 Concession 1 | Amherstburg | Municipal Sewage | Windsor | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 30 | mg/L | mon avg | 1 | 32 | 32 | Action Plan Submitted - Implementing Improvements; Other | Provincial Officer's Order Issued
The Corporation of the Town of Amherstburg -McGregor Sewage Lagoon | Lot 5 Concession 8 West of Walker Road | Amherstburg | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 5.6 | kg/d | mon avg | 1 | 5.726 | 5.726 | Conducting Study | Assessment Complete - No Action Required
The Corporation of the Town of Arnprior - Arnprior Water Pollution Control Plant | Victoria and Albert St Arnprior | Arnprior | Municipal Sewage | Ottawa | ACUTE LETHALITY - DAPHNIA | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-31 | Pass | acute toxicity | /mon | 1 | Fail | Fail | New/Modified Sampling Program Underway | Assessment Complete - Incident Resolved
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | BIOCHEMICAL OXYGEN DEMAND | Order Non-Compliance | 2014-01-01 | 2014-01-31 | 339 | kg | mon avg | 1 | 733.75 | 733.75 | New Equipment or Treatment Process Installed; Other | Director's Order Issued
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | BIOCHEMICAL OXYGEN DEMAND | Order Non-Compliance | 2014-02-01 | 2014-02-28 | 339 | kg | mon avg | 1 | 1542.56 | 1542.56 | New Equipment or Treatment Process Installed | Director's Order Issued
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | BIOCHEMICAL OXYGEN DEMAND | Order Non-Compliance | 2014-04-01 | 2014-04-30 | 2089 | kg | mon avg | 1 | 2471.98 | 2471.98 | New Equipment or Treatment Process Installed | Director's Order Issued
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | BIOCHEMICAL OXYGEN DEMAND | Order Non-Compliance | 2014-09-01 | 2014-09-30 | 320 | kg | mon avg | 1 | 324.72 | 324.72 | New Equipment or Treatment Process Installed | Director's Order Issued
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | BIOCHEMICAL OXYGEN DEMAND | Order Non-Compliance | 2014-12-01 | 2014-12-31 | 460 | kg | mon avg | 1 | 808.81 | 808.81 | New Equipment or Treatment Process Installed | Director's Order Issued
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | PHOSPHORUS, TOTAL | Order Non-Compliance | 2014-01-01 | 2014-01-31 | 23 | kg | mon avg | 1 | 101.04 | 101.04 | New Equipment or Treatment Process Installed | Director's Order Issued
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | PHOSPHORUS, TOTAL | Order Non-Compliance | 2014-02-01 | 2014-02-28 | 20 | kg | mon avg | 1 | 116.26 | 116.26 | New Equipment or Treatment Process Installed | Director's Order Issued
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | PHOSPHORUS, TOTAL | Order Non-Compliance | 2014-02-01 | 2014-02-28 | 1.5 | mg/L | mon avg | 1 | 1.65 | 1.65 | New Equipment or Treatment Process Installed | Director's Order Issued
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | PHOSPHORUS, TOTAL | Order Non-Compliance | 2014-04-01 | 2014-04-30 | 125 | kg | mon avg | 1 | 164.69 | 164.69 | New Equipment or Treatment Process Installed | Director's Order Issued
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | PHOSPHORUS, TOTAL | Order Non-Compliance | 2014-09-01 | 2014-09-30 | 19 | kg | mon avg | 1 | 20.16 | 20.16 | New Equipment or Treatment Process Installed | Director's Order Issued
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | PHOSPHORUS, TOTAL | Order Non-Compliance | 2014-10-01 | 2014-10-31 | 30 | kg | mon avg | 1 | 33.95 | 33.95 | New Equipment or Treatment Process Installed | Director's Order Issued
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | PHOSPHORUS, TOTAL | Order Non-Compliance | 2014-12-01 | 2014-12-31 | 28 | kg | mon avg | 1 | 69.7 | 69.7 | New Equipment or Treatment Process Installed | Director's Order Issued
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | TOTAL SUSPENDED SOLIDS | Order Non-Compliance | 2014-02-01 | 2014-02-28 | 339 | kg | mon avg | 1 | 518.88 | 518.88 | New Equipment or Treatment Process Installed | Director's Order Issued
The Corporation of the Town of Cobalt - Cobalt Constructed Wetland | 100 Hudson Bay Rd | Cobalt | Municipal Sewage | North Bay | TOTAL SUSPENDED SOLIDS | Order Non-Compliance | 2014-09-01 | 2014-09-30 | 320 | kg | mon avg | 1 | 410.91 | 410.91 | New Equipment or Treatment Process Installed | Director's Order Issued
The Corporation of the Town of Cochrane - Cochrane Sewage Treatment Plant | PCL 2688 former Township of Glackmeyer | Cochrane | Municipal Sewage | Timmins | BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 20 | mg/L | rolling avg | 1 | 62.89 | 62.89 | None Required | Assessment Complete - No Action Required
The Corporation of the Town of Cochrane - Cochrane Sewage Treatment Plant | PCL 2688 former Township of Glackmeyer | Cochrane | Municipal Sewage | Timmins | BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 20 | mg/L | rolling avg | 1 | 62.95 | 62.95 | None Required | Voluntary Abatement Program Underway
The Corporation of the Town of Cochrane - Cochrane Sewage Treatment Plant | PCL 2688 former Township of Glackmeyer | Cochrane | Municipal Sewage | Timmins | BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-31 | 20 | mg/L | rolling avg | 1 | 60.98 | 60.98 | None Required | Voluntary Abatement Program Underway
The Corporation of the Town of Cochrane - Cochrane Sewage Treatment Plant | PCL 2688 former Township of Glackmeyer | Cochrane | Municipal Sewage | Timmins | BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-06-01 | 2014-06-30 | 20 | mg/L | rolling avg | 1 | 60.14 | 60.14 | Action Plan Submitted - Implementing Improvements; None Required | Voluntary Abatement Program Underway
The Corporation of the Town of Cochrane - Cochrane Sewage Treatment Plant | PCL 2688 former Township of Glackmeyer | Cochrane | Municipal Sewage | Timmins | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 20 | mg/L | rolling avg | 1 | 214.32 | 214.32 | None Required | Assessment Complete - No Action Required
The Corporation of the Town of Cochrane - Cochrane Sewage Treatment Plant | PCL 2688 former Township of Glackmeyer | Cochrane | Municipal Sewage | Timmins | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 20 | mg/L | rolling avg | 1 | 213.15 | 213.15 | None Required | Voluntary Abatement Program Underway
The Corporation of the Town of Cochrane - Cochrane Sewage Treatment Plant | PCL 2688 former Township of Glackmeyer | Cochrane | Municipal Sewage | Timmins | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-31 | 20 | mg/L | rolling avg | 1 | 205.35 | 205.35 | None Required | Voluntary Abatement Program Underway
The Corporation of the Town of Cochrane - Cochrane Sewage Treatment Plant | PCL 2688 former Township of Glackmeyer | Cochrane | Municipal Sewage | Timmins | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-06-01 | 2014-06-30 | 20 | mg/L | rolling avg | 1 | 196.73 | 196.73 | Action Plan Submitted - Implementing Improvements; None Required | Voluntary Abatement Program Underway
The Corporation of the Town of Deep River -Deep River Sewage Treatment Plant | 1 Cedar Rd | Deep River | Municipal Sewage | Ottawa | ACUTE LETHALITY - DAPHNIA | Approval/Permit Non-Compliance | 2014-03-05 | 2014-03-05 | Pass | acute toxicity | /quart | 1 | Fail | Fail | Additional Monitoring Underway | Assessment Underway
The Corporation of the Town of Deep River -Deep River Sewage Treatment Plant | 1 Cedar Rd | Deep River | Municipal Sewage | Ottawa | ACUTE LETHALITY - TROUT | Approval/Permit Non-Compliance | 2014-03-05 | 2014-03-05 | Pass | acute toxicity | /quart | 1 | Fail | Fail | Additional Monitoring Underway | Assessment Underway
The Corporation of the Town of Hanover - Hanover Water Pollution Control Plant | 718 7th Ave | Hanover | Municipal Sewage | Owen Sound | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 201 | 201 | Additional Monitoring Underway | Voluntary Abatement Program Underway
The Corporation of the Town of Hearst -Hearst Sewage Treatment Lagoons | RP 6R-1719 Township of Kendall | Kendall | Municipal Sewage | Timmins | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-03-24 | 2014-03-24 | 1.27 | kg | /d | 1 | 1.81 | 1.81 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Town of Iroquois Falls - Iroquois Falls Sewage Treatment Plant | 2 Northwest Industrial Rd | Iroquois Falls | Municipal Sewage | Timmins | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-05-13 | 2014-06-13 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 231 | 231 | Operational Process Modification | Other Abatement Action Taken
The Corporation of the Town of Iroquois Falls - Iroquois Falls Sewage Treatment Plant | 2 Northwest Industrial Rd | Iroquois Falls | Municipal Sewage | Timmins | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-08-01 | 2014-08-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 346 | 346 | Operational Process Modification | Assessment Complete - Incident Resolved
The Corporation of the Town of Iroquois Falls - Iroquois Falls Sewage Treatment Plant | 2 Northwest Industrial Rd | Iroquois Falls | Municipal Sewage | Timmins | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 1007 | 1007 | Operational Process Modification | Assessment Complete - Incident Resolved
The Corporation of the Town of Kingsville - Cottam Lagoon | 168 Belle River Rd | Kingsville | Municipal Sewage | Windsor | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 5724 | 5724 | Additional Monitoring Underway | Assessment Complete - No Action Required
The Corporation of the Town of Kingsville - Cottam Lagoon | 168 Belle River Rd | Kingsville | Municipal Sewage | Windsor | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 748 | 748 | Additional Monitoring Underway | Assessment Complete - No Action Required
The Corporation of the Town of Kingsville - Cottam Lagoon | 168 Belle River Rd | Kingsville | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 4 | mg/L | mon avg | 1 | 8.79 | 8.79 | Additional Monitoring Underway | Assessment Complete - No Action Required
The Corporation of the Town of Kingsville - Cottam Lagoon | 168 Belle River Rd | Kingsville | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 4 | mg/L | mon avg | 1 | 8.81 | 8.81 | Conducting Study; Operational Process Modification | Assessment Underway
The Corporation of the Town of Kingsville - Cottam Lagoon | 168 Belle River Rd | Kingsville | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 4 | mg/L | mon avg | 1 | 7.35 | 7.35 | Additional Monitoring Underway | Assessment Complete - No Action Required
The Corporation of the Town of Kingsville - Cottam Lagoon | 168 Belle River Rd | Kingsville | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 4 | mg/L | mon avg | 1 | 7.35 | 7.35 | Conducting Study; Operational Process Modification | Assessment Underway
The Corporation of the Town of Kingsville - Cottam Lagoon | 168 Belle River Rd | Kingsville | Municipal Sewage | Windsor | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 2 | mg/L | mon avg | 1 | 7.54 | 7.54 | Additional Monitoring Underway | Assessment Complete - No Action Required
The Corporation of the Town of Mattawa - Mattawa WPCP | Lot: 38 & 39, Concession: 1, Geographic Township: MATTAWAN | Mattawa | Municipal Sewage | North Bay | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 2.5 | mg/L | mon avg | 1 | 3.36 | 3.36 | Action Plan Submitted - Implementing Improvements; Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Town of Mattawa - Mattawa WPCP | Lot: 38 & 39, Concession: 1, Geographic Township: MATTAWAN | Mattawa | Municipal Sewage | North Bay | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 2.5 | mg/L | mon avg | 1 | 2.91 | 2.91 | Equipment Modified - Repaired - Replaced or Re-calibrated | Voluntary Abatement Program Underway
The Corporation of the Town of New Tecumseth - Tottenham Wastewater Treatment Plant | 6830 4th Line | New Tecumseth | Municipal Sewage | Barrie | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 3.3 | mg/L | mon avg | 1 | 16.1 | 16.1 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Town of New Tecumseth - Tottenham Wastewater Treatment Plant | 6830 4th Line | New Tecumseth | Municipal Sewage | Barrie | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 3.3 | mg/L | mon avg | 1 | 25.6 | 25.6 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Town of New Tecumseth - Tottenham Wastewater Treatment Plant | 6830 4th Line | New Tecumseth | Municipal Sewage | Barrie | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 3.3 | mg/L | mon avg | 1 | 18.3 | 18.3 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Town of New Tecumseth - Tottenham Wastewater Treatment Plant | 6830 4th Line | New Tecumseth | Municipal Sewage | Barrie | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 1.2 | mg/L | mon avg | 1 | 2 | 2 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Town of New Tecumseth - Tottenham Wastewater Treatment Plant | 6830 4th Line | New Tecumseth | Municipal Sewage | Barrie | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-08-01 | 2014-08-31 | 0.5 | mg/L | mon avg | 1 | 1.1 | 1.1 | New/Amended Approval | Assessment Complete - No Action Required
The Corporation of the Town of New Tecumseth - Tottenham Wastewater Treatment Plant | 6830 4th Line | New Tecumseth | Municipal Sewage | Barrie | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-12-01 | 2014-12-31 | 3.3 | mg/L | mon avg | 1 | 3.8 | 3.8 | New/Amended Approval | Assessment Complete - No Action Required
The Corporation of the Town of Petrolia -Petrolia Wastewater Treatment Plant | 546 Maude St | Petrolia | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-31 | 3 | mg/L | mon avg | 1 | 3.08 | 3.08 | Operational Process Modification | Assessment Complete - Incident Resolved
The Corporation of the Town of Petrolia -Petrolia Wastewater Treatment Plant | 546 Maude St | Petrolia | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 3 | mg/L | mon avg | 1 | 4.06 | 4.06 | Operational Process Modification | Assessment Complete - Incident Resolved
The Corporation of the Town of Petrolia -Petrolia Wastewater Treatment Plant | 546 Maude St | Petrolia | Municipal Sewage | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-08-01 | 2014-08-31 | 3 | mg/L | mon avg | 1 | 3.22 | 3.22 | Operational Process Modification | Assessment Complete - Incident Resolved
The Corporation of the Town of Smooth Rock Falls -Smooth Rock Falls Sewage Treatment Plant | 110 First St | Smooth Rock Falls | Municipal Sewage | Timmins | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 27000 | 27000 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the Town of Smooth Rock Falls -Smooth Rock Falls Sewage Treatment Plant | 110 First St | Smooth Rock Falls | Municipal Sewage | Timmins | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 25 | mg/L | mon avg | 1 | 43 | 43 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the Town of South Bruce Peninsula - Wiarton Sewage Lagoon System | 441048 Elm St | South Bruce | Municipal Sewage | Owen Sound | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 0.5 | mg/L | mon avg | 2 | 0.87 | 0.94 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - No Action Required
The Corporation of the Town of South Bruce Peninsula - Wiarton Sewage Lagoon System | 441048 Elm St | South Bruce | Municipal Sewage | Owen Sound | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 0.5 | mg/L | mon avg | 1 | 0.58 | 0.58 | None Required | Assessment Complete - No Action Required
The Corporation of the Town of South Bruce Peninsula - Wiarton Sewage Lagoon System | 441048 Elm St | South Bruce | Municipal Sewage | Owen Sound | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 24 | mg/L | mon avg | 1 | 25.8 | 25.8 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Town of Tecumseh - Skyway Subdivision Wastewater Treatment Facility | McCord Lane | Tecumseh | Municipal Sewage | Windsor | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-06-01 | 2014-06-30 | 10 | mg/L | mon avg | 1 | 15 | 15 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of Alfred and Plantagenet - Village of Plantagenet sewage treatment lagoon | Concession 5 Road Village of Plantagenet | Alfred and Plantagenet | Municipal Sewage | Cornwall | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-05-31 | 25 | mg/L | seasonal avg | 1 | 39.625 | 39.625 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of Alfred and Plantagenet - Village of Plantagenet sewage treatment lagoon | Concession 5 Road Village of Plantagenet | Alfred and Plantagenet | Municipal Sewage | Cornwall | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-11-17 | 2014-12-04 | 25 | mg/L | seasonal avg | 1 | 54.3 | 54.3 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of Asphodel-Norwood - Norwood Water Pollution Control Plant | 34 Industrial Dr | Asphodel-Norwood | Municipal Sewage | Peterborough | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-09-01 | 2014-09-01 | 0.24 | mg/L | /d | 1 | 0.46 | 0.46 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the Township of Assiginack - Manitowaning Lagoon | Lot: 41 & 42, Concession: 1, Geographic Township: ASSIGINACK | Assiginack | Municipal Sewage | Sudbury | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 1 | mg/L | mon avg | 1 | 1.625 | 1.625 | New/Modified Sampling Program Underway; Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Township of Assiginack - Manitowaning Lagoon | Lot: 41 & 42, Concession: 1, Geographic Township: ASSIGINACK | Assiginack | Municipal Sewage | Sudbury | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-06-01 | 2014-06-30 | 1 | mg/L | mon avg | 1 | 2.315 | 2.315 | New/Modified Sampling Program Underway; Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Township of Assiginack - Manitowaning Lagoon | Lot: 41 & 42, Concession: 1, Geographic Township: ASSIGINACK | Assiginack | Municipal Sewage | Sudbury | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-09-01 | 2014-09-30 | 1 | mg/L | mon avg | 1 | 1.345 | 1.345 | New/Modified Sampling Program Underway; Operational Process Modification | Assessment Complete - Incident Resolved; Assessment Complete - No Action Required
The Corporation of the Township of Assiginack - Manitowaning Lagoon | Lot: 41 & 42, Concession: 1, Geographic Township: ASSIGINACK | Assiginack | Municipal Sewage | Sudbury | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 1 | mg/L | mon avg | 1 | 1.28 | 1.28 | New/Modified Sampling Program Underway; Operational Process Modification | Assessment Complete - Incident Resolved; Assessment Complete - No Action Required
The Corporation of the Township of Assiginack - Manitowaning Lagoon | Lot: 41 & 42, Concession: 1, Geographic Township: ASSIGINACK | Assiginack | Municipal Sewage | Sudbury | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 40 | mg/L | mon avg | 1 | 41 | 41 | New/Modified Sampling Program Underway; Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Township of Centre Wellington - Elora Wastewater Treatment Plant | 49 Guelph Rd | Centre Wellington | Municipal Sewage | Guelph | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 826.1 | 826.1 | New Equipment or Treatment Process Installed | Voluntary Abatement Program Underway
The Corporation of the Township of Centre Wellington - Elora Wastewater Treatment Plant | 49 Guelph Rd | Centre Wellington | Municipal Sewage | Guelph | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 293 | 293 | None Required | Voluntary Abatement Program Underway
The Corporation of the Township of Centre Wellington - Elora Wastewater Treatment Plant | 49 Guelph Rd | Centre Wellington | Municipal Sewage | Guelph | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 1392 | 1392 | Equipment Modified - Repaired - Replaced or Re-calibrated | Voluntary Abatement Program Underway
The Corporation of the Township of Champlain - Vankleek Hill Water Pollution Control Plant | 6489 Newton Rd Vankleek Hill | Champlain | Municipal Sewage | Cornwall | FLOW | Approval/Permit Non-Compliance | 2014-04-08 | 2014-04-08 | 4949 | m³ | /d | 1 | 5559 | 5559 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of Champlain - Vankleek Hill Water Pollution Control Plant | 6489 Newton Rd Vankleek Hill | Champlain | Municipal Sewage | Cornwall | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-11-03 | 2014-12-02 | 1 | mg/L | seasonal avg | 1 | 1.01 | 1.01 | Training/Procedure Change | Assessment Complete - No Action Required
The Corporation of the Township of Champlain - Vankleek Hill Water Pollution Control Plant | 6489 Newton Rd Vankleek Hill | Champlain | Municipal Sewage | Cornwall | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-11-03 | 2014-11-06 | 1.7 | mg/L | any | 3 | 3.42 | 3.95 | None Required | Voluntary Abatement Program Underway
The Corporation of the Township of Champlain - Vankleek Hill Water Pollution Control Plant | 6489 Newton Rd Vankleek Hill | Champlain | Municipal Sewage | Cornwall | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-11-10 | 2014-11-13 | 1.7 | mg/L | any | 3 | 3.53 | 3.72 | None Required | Voluntary Abatement Program Underway
The Corporation of the Township of Champlain - Vankleek Hill Water Pollution Control Plant | 6489 Newton Rd Vankleek Hill | Champlain | Municipal Sewage | Cornwall | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-11-17 | 2014-11-20 | 1.7 | mg/L | any | 3 | 2.79 | 3.48 | None Required | Voluntary Abatement Program Underway
The Corporation of the Township of Champlain - Vankleek Hill Water Pollution Control Plant | 6489 Newton Rd Vankleek Hill | Champlain | Municipal Sewage | Cornwall | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-11-24 | 2014-11-27 | 1.7 | mg/L | any | 3 | 3.1 | 3.58 | None Required | Voluntary Abatement Program Underway
The Corporation of the Township of Clearview -Stayner Sewage Treatment Plant | 300 Mowatt St N Stayner | Clearview | Municipal Sewage | Barrie | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 0.4 | mg/L | mon avg | 1 | 0.61 | 0.61 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Township of Clearview -Stayner Sewage Treatment Plant | 300 Mowatt St N Stayner | Clearview | Municipal Sewage | Barrie | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 0.65 | kg/d | mon avg | 1 | 0.99 | 0.99 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Township of Clearview -Stayner Sewage Treatment Plant | 300 Mowatt St N Stayner | Clearview | Municipal Sewage | Barrie | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 0.4 | mg/L | mon avg | 1 | 0.53 | 0.53 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Township of Clearview -Stayner Sewage Treatment Plant | 300 Mowatt St N Stayner | Clearview | Municipal Sewage | Barrie | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 4 | mg/L | mon avg | 1 | 4.62 | 4.62 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Township of Cramahe - Colborne Water Pollution Control Plant | 1108 Ontario Street | Cramahe | Municipal Sewage | Peterborough | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 1936 | 1936 | Additional Monitoring Underway; Operational Process Modification | Assessment Underway
The Corporation of the Township of Cramahe - Colborne Water Pollution Control Plant | 1108 Ontario Street | Cramahe | Municipal Sewage | Peterborough | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-09-01 | 2014-09-30 | 1.2 | kg/d | mon avg | 1 | 1.39 | 1.39 | Operational Process Modification | Assessment Underway
The Corporation of the Township of Cramahe - Colborne Water Pollution Control Plant | 1108 Ontario Street | Cramahe | Municipal Sewage | Peterborough | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-09-01 | 2014-09-30 | 0.7 | mg/L | mon avg | 1 | 0.88 | 0.88 | Operational Process Modification | Assessment Underway
The Corporation of the Township of Cramahe - Colborne Water Pollution Control Plant | 1108 Ontario Street | Cramahe | Municipal Sewage | Peterborough | TOTAL RESIDUAL CHLORINE | Approval/Permit Non-Compliance | 2014-08-01 | 2014-08-31 | 0.02 | mg/L | mon avg | 1 | 0.03 | 0.03 | Operational Process Modification | Assessment Complete - Incident Resolved
The Corporation of the Township of Cramahe - Colborne Water Pollution Control Plant | 1108 Ontario Street | Cramahe | Municipal Sewage | Peterborough | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 43.8 | kg/d | mon avg | 1 | 59.468 | 59.468 | Operational Process Modification; Training/Procedure Change | Voluntary Abatement Program Underway
The Corporation of the Township of Cramahe - Colborne Water Pollution Control Plant | 1108 Ontario Street | Cramahe | Municipal Sewage | Peterborough | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-31 | 43.8 | kg/d | mon avg | 1 | 44.369 | 44.369 | Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Township of Cramahe - Colborne Water Pollution Control Plant | 1108 Ontario Street | Cramahe | Municipal Sewage | Peterborough | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-06-01 | 2014-06-30 | 43.8 | kg/d | mon avg | 1 | 44.873 | 44.873 | Equipment Modified - Repaired - Replaced or Re-calibrated; Operational Process Modification | Voluntary Abatement Program Underway
The Corporation of the Township of Ear Falls - Ear Falls Waste Water Treatment Plant | KM275 Part 1 Aspen St | Ear Falls | Municipal Sewage | Kenora | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 329 | 329 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the Township of Ear Falls - Ear Falls Waste Water Treatment Plant | KM275 Part 1 Aspen St | Ear Falls | Municipal Sewage | Kenora | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-01-01 | 2014-12-31 | 25 | mg/L | annual avg | 1 | 27.9 | 27.9 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - No Action Required
The Corporation of the Township of East Hawkesbury - Chute a Blondeau sewage treatment plant | Lot: 18, Concession: 1, Geographic Township: EAST HAWKESBURY | East Hawkesbury | Municipal Sewage | Cornwall | FLOW | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-01 | 109 | m³ | /d | 1 | 111 | 111 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of East Luther Grand Valley - Grand Valley Wastewater Treatment Plant | Industrial Rd Part of Lot 31 Concession 1 and Part of Lot 31 Consession 2 | East Luther Grand Valley | Municipal Sewage | Guelph | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 0.15 | mg/L | mon avg | 1 | 0.32 | 0.32 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of East Luther Grand Valley - Grand Valley Wastewater Treatment Plant | Industrial Rd Part of Lot 31 Concession 1 and Part of Lot 31 Consession 2 | East Luther Grand Valley | Municipal Sewage | Guelph | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 0.19 | kg/d | mon avg | 1 | 0.63 | 0.63 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of East Luther Grand Valley - Grand Valley Wastewater Treatment Plant | Industrial Rd Part of Lot 31 Concession 1 and Part of Lot 31 Consession 2 | East Luther Grand Valley | Municipal Sewage | Guelph | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 1 | mg/L | mon avg | 1 | 1.2 | 1.2 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of East Luther Grand Valley - Grand Valley Wastewater Treatment Plant | Industrial Rd Part of Lot 31 Concession 1 and Part of Lot 31 Consession 2 | East Luther Grand Valley | Municipal Sewage | Guelph | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 1.24 | kg/d | mon avg | 1 | 2.28 | 2.28 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of East Luther Grand Valley - Grand Valley Wastewater Treatment Plant | Industrial Rd Part of Lot 31 Concession 1 and Part of Lot 31 Consession 2 | East Luther Grand Valley | Municipal Sewage | Guelph | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 10 | mg/L | mon avg | 1 | 24.8 | 24.8 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of East Luther Grand Valley - Grand Valley Wastewater Treatment Plant | Industrial Rd Part of Lot 31 Concession 1 and Part of Lot 31 Consession 2 | East Luther Grand Valley | Municipal Sewage | Guelph | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 12.4 | kg/d | mon avg | 1 | 47.84 | 47.84 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of Fauquier-Strickland - Fauquier-Strickland Sewage Lagoon | 25 Grzela Rd | Fauquier-Strickland | Municipal Sewage | Timmins | PH - HIGH | Approval/Permit Non-Compliance | 2014-07-02 | 2014-07-02 | 9 | pH | any | 1 | 9.7 | 9.7 | Ceased Operations | Voluntary Abatement Program Underway
The Corporation of the Township of Huron-Kinloss - Ripley Lagoons | Lot: Part of Lot 14, Concession: 7, Geographic Township: HURON | Huron-Kinloss | Municipal Sewage | Owen Sound | AMMONIA, UNIONIZED | Approval/Permit Non-Compliance | 2014-04-16 | 2014-04-23 | 0.02 | mg/L | any | 2 | 0.037 | 0.037 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of Huron-Kinloss -Lucknow Sewage Treatment Facility | Lot: 53 54 55, Concession: 1 Geographic Township: KINLOSS | Huron-Kinloss | Municipal Sewage | Owen Sound | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-30 | 5 | mg/L | mon avg | 1 | 6 | 6 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of Loyalist - Amherstview WPCP | Taylor Kidd Rd (Lot 37 Concession 1) | Loyalist | Municipal Sewage | Kingston | PH - HIGH | Approval/Permit Non-Compliance | 2014-03-25 | 2014-10-16 | 9.5 | pH | any | 83 | 9.7 | 10.9 | Conducting Study; New/Amended Approval | Voluntary Abatement Program Underway
The Corporation of the Township of Loyalist -Bath Water Pollution Control Plant | 50 Sir John Johnson Dr Bath | Loyalist | Municipal Sewage | Kingston | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 1 | mg/L | mon avg | 1 | 1.14 | 1.14 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the Township of Loyalist -Bath Water Pollution Control Plant | 50 Sir John Johnson Dr Bath | Loyalist | Municipal Sewage | Kingston | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 1 | mg/L | mon avg | 1 | 1.09 | 1.09 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the Township of Madawaska Valley -Barry's Bay Sewage Treatment Plant | 34 Lakeshore Dr | Madawaska Valley | Municipal Sewage | Ottawa | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 0.2 | mg/L | mon avg | 1 | 0.208 | 0.208 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Township of Manitouwadge - Manitouwadge Sewage Treatment Facility | Lot M179 Conc BLKA Manitouwadge Township | Manitouwadge | Municipal Sewage | Thunder Bay | FLOW | Approval/Permit Non-Compliance | 2014-04-30 | 2014-05-01 | 4100 | m³ | /d | 1 | 5185 | 5185 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Township of Manitouwadge - Manitouwadge Sewage Treatment Facility | Lot M179 Conc BLKA Manitouwadge Township | Manitouwadge | Municipal Sewage | Thunder Bay | FLOW | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-02 | 4100 | m³ | /d | 1 | 4745 | 4745 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Township of Manitouwadge - Manitouwadge Sewage Treatment Facility | Lot M179 Conc BLKA Manitouwadge Township | Manitouwadge | Municipal Sewage | Thunder Bay | FLOW | Approval/Permit Non-Compliance | 2014-05-02 | 2014-05-03 | 4100 | m³ | /d | 1 | 5016 | 5016 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Township of Manitouwadge - Manitouwadge Sewage Treatment Facility | Lot M179 Conc BLKA Manitouwadge Township | Manitouwadge | Municipal Sewage | Thunder Bay | FLOW | Approval/Permit Non-Compliance | 2014-05-03 | 2014-05-04 | 4100 | m³ | /d | 1 | 5399 | 5399 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Township of Manitouwadge - Manitouwadge Sewage Treatment Facility | Lot M179 Conc BLKA Manitouwadge Township | Manitouwadge | Municipal Sewage | Thunder Bay | FLOW | Approval/Permit Non-Compliance | 2014-05-04 | 2014-05-05 | 4100 | m³ | /d | 1 | 4423 | 4423 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Township of Manitouwadge - Manitouwadge Sewage Treatment Facility | Lot M179 Conc BLKA Manitouwadge Township | Manitouwadge | Municipal Sewage | Thunder Bay | FLOW | Approval/Permit Non-Compliance | 2014-06-02 | 2014-06-03 | 4100 | m³ | /d | 1 | 4176.89 | 4176.89 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Township of Manitouwadge - Manitouwadge Sewage Treatment Facility | Lot M179 Conc BLKA Manitouwadge Township | Manitouwadge | Municipal Sewage | Thunder Bay | FLOW | Approval/Permit Non-Compliance | 2014-06-03 | 2014-06-04 | 4100 | m³ | /d | 1 | 4138.88 | 4138.88 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of Manitouwadge - Manitouwadge Sewage Treatment Facility | Lot M179 Conc BLKA Manitouwadge Township | Manitouwadge | Municipal Sewage | Thunder Bay | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-22 | 2014-04-22 | 30 | mg/L | /2wk | 1 | 41.7 | 41.7 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Township of Marathon - Marathon WPCP | 4 Hemlo Dr | Marathon | Municipal Sewage | Thunder Bay | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-01-07 | 2014-12-22 | 1 | mg/L | /d | 26 | 3.59 | 3.59 | New/Amended Approval | Assessment Underway
The Corporation of the Township of McGarry - McGarry Sewage Treatment System | McGarry Mining Claim MC L5414 PCL 348CST | McGarry | Municipal Sewage | Timmins | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-03-01 | 2014-03-31 | 0.5 | mg/L | mon avg | 1 | 0.516 | 0.516 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of McGarry - McGarry Sewage Treatment System | McGarry Mining Claim MC L5414 PCL 348CST | McGarry | Municipal Sewage | Timmins | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 0.6 | kg/d | mon avg | 1 | 1.045 | 1.045 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Township of McGarry - McGarry Sewage Treatment System | McGarry Mining Claim MC L5414 PCL 348CST | McGarry | Municipal Sewage | Timmins | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 0.6 | kg/d | mon avg | 1 | 0.707 | 0.707 | Other | Assessment Complete - No Action Required
The Corporation of the Township of North Dundas - Chesterville Sewage Lagoon | 636 St. Lawrence St | North Dundas | Municipal Sewage | Cornwall | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-10-10 | 2014-10-21 | 30 | mg/L | seasonal avg | 1 | 47.3 | 47.3 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of North Glengarry - Alexandria Sewage Works | McCormick Rd | North Glengarry | Municipal Sewage | Cornwall | TOTAL RESIDUAL CHLORINE | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-09 | 0.02 | mg/L | mon avg | 2 | 0.064 | 0.064 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - No Action Required
The Corporation of the Township of North Huron - Blyth Wastewater Treatment Plant | Lot 42 Concession 1 | North Huron | Municipal Sewage | Owen Sound | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 200 | CT/100mL | mon avg. on a geo. mean density | 1 | 311 | 311 | Equipment Modified - Repaired - Replaced or Re-calibrated; Other | Voluntary Abatement Program Underway
The Corporation of the Township of Perth East - Milverton WPCP | Mill Street Lot 5 Conc. 3 | Perth East | Municipal Sewage | London | CARBONACEOUS BIOCHEMICAL OXYGEN DEMAND | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 15 | mg/L | mon avg | 1 | 25 | 25 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Township of Perth East - Milverton WPCP | Mill Street Lot 5 Conc. 3 | Perth East | Municipal Sewage | London | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 1 | mg/L | mon avg | 1 | 1.5 | 1.5 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Township of Perth East - Shakespeare Wastewater Treatment Plant | 3976 Galt St Perth East | Perth East | Municipal Sewage | London | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-31 | 0.3 | mg/L | mon avg | 1 | 0.32 | 0.32 | Operational Process Modification | Assessment Complete - Incident Resolved
The Corporation of the Township of Perth East - Shakespeare Wastewater Treatment Plant | 3976 Galt St Perth East | Perth East | Municipal Sewage | London | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-31 | 0.3 | mg/L | mon avg | 1 | 0.32 | 0.32 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Township of Perth East - Shakespeare Wastewater Treatment Plant | 3976 Galt St Perth East | Perth East | Municipal Sewage | London | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 0.3 | mg/L | mon avg | 1 | 0.355 | 0.355 | Operational Process Modification | Assessment Complete - Incident Resolved
The Corporation of the Township of Perth East - Shakespeare Wastewater Treatment Plant | 3976 Galt St Perth East | Perth East | Municipal Sewage | London | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 3 | mg/L | mon avg | 1 | 9.33 | 9.33 | Equipment Modified - Repaired - Replaced or Re-calibrated; Operational Process Modification | Assessment Underway
The Corporation of the Township of Red Rock - Red Rock STP | 10 Rankin St | Red Rock | Municipal Sewage | Thunder Bay | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-01-01 | 2014-12-31 | 1 | mg/L | mon avg | 8 | 2.05 | 2.05 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the Township of Sables-Spanish Rivers - Webbwood Sewage Lagoon | Lot: 9, Concession: 6, Geographic Township: Hallam | Hallam | Municipal Sewage | Sudbury | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-12-08 | 2014-12-11 | 1 | mg/L | seasonal avg | 1 | 2.1 | 2.1 | Other | Assessment Complete - Incident Resolved
The Corporation of the Township of Severn - Coldwater Wastewater Treatment Plant | 1130 Upper Big Chute Rd | Severn | Municipal Sewage | Barrie | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 15 | mg/L | mon avg | 1 | 28.3 | 28.3 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the Township of Severn - Coldwater Wastewater Treatment Plant | 1130 Upper Big Chute Rd | Severn | Municipal Sewage | Barrie | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 13.8 | kg/d | mon avg | 1 | 19.1 | 19.1 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Corporation of the Township of Severn - Coldwater Wastewater Treatment Plant | 1130 Upper Big Chute Rd | Severn | Municipal Sewage | Barrie | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 13.8 | kg/d | mon avg | 1 | 16.2 | 16.2 | Additional Monitoring Underway | Assessment Complete - Incident Resolved
The Corporation of the Township of Severn - Washago WPCP | Lot: 10, Concession: 15, Geographical Township: Severn | Severn | Municipal Sewage | Barrie | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-12 | 1024 | kg/d | seasonal avg | 1 | 1344 | 1344 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of Severn - Washago WPCP | Lot: 10, Concession: 15, Geographical Township: Severn | Severn | Municipal Sewage | Barrie | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-05-01 | 2014-05-12 | 25 | mg/L | seasonal avg | 1 | 28 | 28 | None Required | Assessment Complete - No Action Required
The Corporation of the Township of South Stormont - Ingleside Wastewater Treatment System | 2 - 15005 County Rd | South Stormont | Municipal Sewage | Cornwall | FLOW | Approval/Permit Non-Compliance | 2014-04-05 | 2014-04-05 | 10027 | m³ | /d | 1 | 11202 | 11202 | Action Plan Submitted - Implementing Improvements | Voluntary Abatement Program Underway
The Corporation of the Township of South Stormont - Ingleside Wastewater Treatment System | 2 - 15005 County Rd | South Stormont | Municipal Sewage | Cornwall | FLOW | Approval/Permit Non-Compliance | 2014-04-08 | 2014-04-08 | 10027 | m³ | /d | 1 | 15483 | 15483 | Conducting Study | Assessment Underway
The Corporation of the Township of South Stormont - Ingleside Wastewater Treatment System | 2 - 15005 County Rd | South Stormont | Municipal Sewage | Cornwall | FLOW | Approval/Permit Non-Compliance | 2014-04-09 | 2014-04-09 | 10027 | m³ | /d | 1 | 10135 | 10135 | Conducting Study | Voluntary Abatement Program Underway
The Corporation of the Township of South Stormont - Ingleside Wastewater Treatment System | 2 - 15005 County Rd | South Stormont | Municipal Sewage | Cornwall | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 1 | mg/L | mon avg | 1 | 1.15 | 1.15 | Other | Voluntary Abatement Program Underway
The Corporation of the Township of Tay - Port McNicoll Wastewater Treatment Plant | 551 First St | Tay | Municipal Sewage | Barrie | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 0.48 | kg/d | mon avg | 1 | 0.78 | 0.78 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Township of Tay - Port McNicoll Wastewater Treatment Plant | 551 First St | Tay | Municipal Sewage | Barrie | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 0.25 | mg/L | mon avg | 1 | 0.47 | 0.47 | None Required | Assessment Complete - Incident Resolved
The Corporation of the Township of Val Rita-Harty - Harty Sewage Lagoon | Lot: 29, Concession: 4, Geographic Township: WILLIAMSON | Val Rita-Harty | Municipal Sewage | Timmins | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-05-26 | 2014-06-30 | 22.5 | mg/L | seasonal avg | 1 | 67.5 | 67.5 | None Required | Assessment Complete - No Action Required
The Corporation of the Village of Burk's Falls -Burk's Falls Lagoon | Lagoon Rd | Burk's Falls | Municipal Sewage | North Bay | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-11-24 | 2014-12-11 | 1 | mg/L | seasonal avg | 1 | 1.77 | 1.77 | Action Plan Submitted - Implementing Improvements | Assessment Underway
The Corporation of the Village of Merrickville-Wolford -Merrickville STP | 106 Collar Hill Rd | Merrickville-Wolford | Municipal Sewage | Kingston | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 0.5 | kg/d | mon avg | 1 | 0.512 | 0.512 | Operational Process Modification | Assessment Complete - No Action Required
The Corporation of the Village of Merrickville-Wolford -Merrickville STP | 106 Collar Hill Rd | Merrickville-Wolford | Municipal Sewage | Kingston | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 12 | kg/d | mon avg | 1 | 21.294 | 21.294 | Operational Process Modification | Assessment Complete - No Action Required
The Forest-Cliff Camps, Incorporated | 8324 Glendale Dr | Lambton Shores | Miscellaneous Communal | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 3 | mg/L | mon avg | 1 | 11.6 | 11.6 | Other | Voluntary Abatement Program Underway
The Forest-Cliff Camps, Incorporated | 8324 Glendale Dr | Lambton Shores | Miscellaneous Communal | Sarnia | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-09-01 | 2014-09-30 | 3 | mg/L | mon avg | 1 | 3.5 | 3.5 | Action Plan Submitted - Implementing Improvements; Conducting Study; Operational Process Modification | Voluntary Abatement Program Underway
The Regional Municipality of Durham - Corbett Creek Water Pollution Control Plant | 2400 Forbes St | Whitby | Municipal Sewage | York-Durham | ESCHERICHIA COLI | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 100 | CT/100mL | mon avg. on a geo. mean density | 1 | 217 | 217 | Operational Process Modification | Voluntary Abatement Program Underway
The Regional Municipality of Durham - Lake Simcoe Water Pollution Control Plant | 885B Concession 5 Rd Thorah | Brock | Municipal Sewage | York-Durham | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-06-01 | 2014-06-30 | 5 | mg/L | mon avg | 1 | 7.6 | 7.6 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - No Action Required
The Regional Municipality of Durham - Nonquon River Water Pollution Control Plant | 1730 Scugog Line 8 | Scugog | Municipal Sewage | York-Durham | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-02-20 | 2014-02-28 | 0.3 | mg/L | mon avg | 1 | 0.69 | 0.69 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - No Action Required
The Regional Municipality of Durham - Uxbridge Brook Water Pollution Control Plant | 129 Main St N | Uxbridge | Municipal Sewage | York-Durham | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 3 | mg/L | mon avg | 1 | 5.07 | 5.07 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Regional Municipality of Durham - Uxbridge Brook Water Pollution Control Plant | 129 Main St N | Uxbridge | Municipal Sewage | York-Durham | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-10-01 | 2014-10-31 | 10.9 | kg/d | mon avg | 1 | 18.8 | 18.8 | Equipment Modified - Repaired - Replaced or Re-calibrated | Assessment Complete - Incident Resolved
The Regional Municipality of Halton - Skyway Wastewater Treatment Plant | 1125 Lakeshore Rd | Burlington | Municipal Sewage | Halton-Peel | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-02-01 | 2014-02-28 | 5.6 | mg/L | mon avg | 1 | 7.48 | 7.48 | Action Plan Submitted - Implementing Improvements | Assessment Complete - No Action Required
The Regional Municipality of Niagara - Grimsby-Baker Road WPCP | 347 Baker Rd | Grimsby | Municipal Sewage | Niagara | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-07-01 | 2014-09-30 | 0.5 | mg/L | mon avg | 3 | 0.55 | 1.07 | Action Plan Submitted - Implementing Improvements | Assessment Complete - Incident Resolved
The Regional Municipality of Niagara - Niagara-on-the-Lake Queenston WPCP | 30 Front St | Niagara-on-the-Lake | Municipal Sewage | Niagara | PH - LOW | Approval/Permit Non-Compliance | 2014-11-09 | 2014-11-11 | 6 | pH | any | 3 | 5.5 | 5.9 | Additional Monitoring Underway | Assessment Complete - Incident Resolved
The Regional Municipality of Niagara - Niagara-on-the-Lake Queenston WPCP | 30 Front St | Niagara-on-the-Lake | Municipal Sewage | Niagara | PHOSPHORUS, TOTAL | Policy/Guideline Non-Conformance | 2014-01-01 | 2014-12-31 | 1 | mg/L | mon avg | 12 | 1.23 | 3 | Action Plan Submitted - Implementing Improvements; New Equipment or Treatment Process Installed; Operational Process Modification | Assessment Complete - Incident Resolved
The Regional Municipality of Niagara - Niagara-on-the-Lake Queenston WPCP | 30 Front St | Niagara-on-the-Lake | Municipal Sewage | Niagara | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-11-01 | 2014-11-30 | 25 | mg/L | mon avg | 1 | 26 | 26 | Operational Process Modification | Assessment Complete - Incident Resolved
The Regional Municipality of Niagara - Niagara-on-the-Lake WPCP | Part 1 and Part 2 Lakeshore Rd | Niagara-on-the-Lake | Municipal Sewage | Niagara | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 1 | mg/L | mon avg | 1 | 1.06 | 1.06 | Action Plan Submitted - Implementing Improvements; Other | Assessment Complete - Incident Resolved
The Regional Municipality of Niagara - Niagara-on-the-Lake WPCP | Part 1 and Part 2 Lakeshore Rd | Niagara-on-the-Lake | Municipal Sewage | Niagara | PHOSPHORUS, TOTAL | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 5.71 | kg/d | mon avg | 1 | 5.79 | 5.79 | Action Plan Submitted - Implementing Improvements; Other | Assessment Complete - Incident Resolved
The Regional Municipality of Niagara - Niagara-on-the-Lake WPCP | Part 1 and Part 2 Lakeshore Rd | Niagara-on-the-Lake | Municipal Sewage | Niagara | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 25 | mg/L | mon avg | 1 | 32.8 | 32.8 | Action Plan Submitted - Implementing Improvements; Other | Assessment Complete - Incident Resolved
The Regional Municipality of Niagara - Niagara-on-the-Lake WPCP | Part 1 and Part 2 Lakeshore Rd | Niagara-on-the-Lake | Municipal Sewage | Niagara | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-31 | 143 | kg/d | mon avg | 1 | 179 | 179 | Action Plan Submitted - Implementing Improvements; Other | Assessment Complete - Incident Resolved
The Regional Municipality of Niagara - Niagara-on-the-Lake WPCP | Part 1 and Part 2 Lakeshore Rd | Niagara-on-the-Lake | Municipal Sewage | Niagara | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 25 | mg/L | mon avg | 1 | 26.4 | 26.4 | Action Plan Submitted - Implementing Improvements; Other | Assessment Complete - Incident Resolved
The Regional Municipality of Niagara - Niagara-on-the-Lake WPCP | Part 1 and Part 2 Lakeshore Rd | Niagara-on-the-Lake | Municipal Sewage | Niagara | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-04-01 | 2014-04-30 | 143 | kg/d | mon avg | 1 | 161.6 | 161.6 | Action Plan Submitted - Implementing Improvements; Other | Assessment Complete - Incident Resolved
The Regional Municipality of Niagara - Niagara-on-the-Lake WPCP | Part 1 and Part 2 Lakeshore Rd | Niagara-on-the-Lake | Municipal Sewage | Niagara | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 25 | mg/L | mon avg | 1 | 29.4 | 29.4 | Action Plan Submitted - Implementing Improvements | Assessment Complete - Incident Resolved
The Regional Municipality of Waterloo - New Hamburg Wastewater Treatment Plant | 1293 Haysville Rd | Wilmot | Municipal Sewage | Guelph | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-08-01 | 2014-08-31 | 1 | mg/L | mon avg | 1 | 1.94 | 1.94 | Equipment Modified - Repaired - Replaced or Re-calibrated; Operational Process Modification | Assessment Complete - Incident Resolved
The Regional Municipality of Waterloo - St. Jacobs WPCP | Princess St E St. Jacobs | Woolwich | Municipal Sewage | Guelph | TOTAL AMMONIA NITROGEN | Approval/Permit Non-Compliance | 2014-01-01 | 2014-01-30 | 2 | mg/L | mon avg | 1 | 2.31 | 2.31 | Operational Process Modification | Voluntary Abatement Program Underway
Unifay Investments Ltd. - Thornton Commercial Plaza | 4171 21 County Road, Thornton | Essa | Miscellaneous Communal | Barrie | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 10 | mg/L | mon avg | 1 | 10.35 | 10.35 | Other | Assessment Complete - Incident Resolved
Windsor Essex Catholic District School Board - St. Thomas of Villanova Secondary School | 2800 North Tline | LaSalle | Miscellaneous Communal | Windsor | TOTAL SUSPENDED SOLIDS | Approval/Permit Non-Compliance | 2014-07-01 | 2014-07-31 | 10 | mg/L | mon avg | 1 | 12.4 | 12.4 | Equipment Modified - Repaired - Replaced or Re-calibrated; Other | Assessment Complete - No Action Required
Ces données sont fournies à titre d’information seulement. Les installations responsables des rejets ont fourni la plupart des données de ce sommaire. Ces installations sont responsables de l’exactitude des données fournies. Certaines données sont aussi dérivées des données du ministère sur les rejets. Les mesures prises par les installations et par le ministère étaient à jour en août 2015. Pour obtenir des données actualisées, veuillez contacter le bureau de district ou de secteur concerné